## Sheet2
Power Meter Tests conducted using an integrative power meter.
Eric Martin MBARI 2015
Test | Supply Voltage (V) | Duration (h) | Power (Wh) | Average Power (W) | Capacity per Day (Ah/day) | Capacity Required for 185 Days +10% (Ah) | No. AA Li Primary Batteries | No. Saft GPS Li Batteries | No. Saft D Tadiran or Xeno Cells | Actual Ah
Office 24hr Window | 6.1 | 24 | 9.72 | 0.405 | 1.5934 | 324.2656 | 327 | 44 | 36 | 342
Quick Test | 4.5 | 0.75 | 0.241 | 0.32133 | 1.7138 | 348.7538 | 351 | 47 | 38 | 361
Chris Wahl #s | 4.5 | 336 | 13.5 | 0.040179 | 0.21429 | 43.6071 | 45 | 6 | 6 | 57
Skylight | 4.5 | 2 | 0.077 | 0.0385 | 0.20533 | 41.7853 | 42 | 6 | 6 | 57
Skylight Test #2 | 4.5 | 24 | 0.81 | 0.03375 | 0.18 | 36.63 | 39 | 5 | 4 | 38
Skylight Test #3 @ 4.5V | 4.5 | 15.1125 | 0.51182 | 0.033867 | 0.18063 | 36.7573 | 39 | 5 | 4 | 38
Skylight Test #4 @ 7.2V | 7.2 | 6 | 0.35176 | 0.058627 | 0.19542 | 39.7684 | 42 | 6 | 6 | 57