# Request for Proposal

# Energy storage system for marine energy converters

Points of Contact:

| Andy Hamilton Monterey Bay Aquarium Research Institute 7700 Sandholdt Road, Moss Landing, CA 95039 Phone: 831-775-1861 hamilton@mbari.org | Chris Bassett Applied Physics Lab., University of Washington 1013 NE 40th St., Seattle, WA 98105 Phone: 206-543-1263 cbassett@uw.edu |
| --- | --- |

November 7, 2024

# Background

The use of environmental energy harvesting in the ocean to support remote charging of vehicles and instrumentation with high power requirements is becoming contingent upon the integration of adequate power storage systems that can accommodate the unique operations of marine energy converters.  The Monterey Bay Aquarium Research Institute has developed a wave-energy converter system that converts energy from the wave-field to electrical energy for the purpose of powering on-buoy instrumentation and re-charging autonomous underwater vehicles that dock to the system (https://link.springer.com/article/10.1007/s40722-021-00197-9).  The University of Washington Applied Physics lab has developed a tidal-turbine lander that sits on the seafloor and harvests energy from tidal flows for similar purposes (https://www.pnnl.gov/publications/first-tidal-turbine-pacific-northwest-signals-wave-future).

The goal of this project is to procure a battery system suitable for integration into these systems, replacing the rudimentary lead-acid battery pack currently in use. Both of these target systems (UW’s Turbine Lander and MBARI’s WEC) are using the same power conversion electronics to create a DC charge voltage from the varying three-phase AC voltages produced by the motors in the respective systems.  Therefore, the battery interface requirements for the two systems are identical.

Some of the challenges associated with leveraging marine energy converters to support at sea loads are (1) high-peak to mean power ratios, (2) rapid charge/discharge requirements for controls optimization, (3) long periods where conditions may result in intermediate states of charge, and (4) requirements for entirely autonomous operation.

For both the wave and tidal energy devices a suitable battery system must accommodate the unusual charge/discharge profile. In addition, both systems are intended to operate autonomously, which imposes additional requirements on its behavior that include ground-fault monitoring, operations during times of low state-of-charge, and unexpected connection/disconnection. This document summarizes the intended system, provides an overall system block diagram, and summarizes requirements on the various components

Appendix A provides some additional details about the wave and tidal harvesting systems this battery system is targeted for, and some examples of the specific charge/discharge profiles that are expected in each system, and some data about the vibration environment. A system overview is included in Figure 1.

Figure 1:  Overall system architecture

# Proposal Request

We are requesting a brief proposal based on the requirements below (and any other information we can provide) outlining how your company will develop and deliver the required battery system.  As we are developing prototype systems, only a handful (qty 2-4) of packs are needed at this time.

Additionally, there are a number of requirements that will be subject to discussion and refinement, and we hope to have a project structure that allows for that. Please include the following items in a proposal:

- Outline of company qualifications and capabilities

- Proposed system specifications. (Architecture, block-diagram, battery voltage range, capacity, battery type, expected lifespan, communication protocol, etc.)

- Proposed project structure (phases, reviews, and acceptance tests)

- Scope of work for project phases and timing.

- Deliverables

- Costs, NRE and per-unit.

- Estimated lead time for full project

- Other terms

# Preliminary Requirements

Figure 1 above illustrates the entire system, and the components inside the “Common Housing” demarcation are what we are interested in procuring.  The requirements below are written to describe the entire battery system.  It is possible that some of these features (Isolation monitoring, switching circuits, etc.) could be supplied by us and we are open to discussion if it makes sense for some components/features to be user-supplied.

Individual subsystem/component requirements are established in the following narrative while Appendix B provides this information in tabular form.

## Batteries

The battery pack itself needs to operate in a voltage range of 270V-350V, 325V nominal, and be able to source/sink up to 35 Amps to be consistent with the motor drive/generators capabilities. The capacity for this system is desired to be in the 10-12 kW-hr range.  There is no specific requirement on chemistry and this can be determined as needed to accommodate the cycle/cycle-life requirements, BMS restrictions given the charge/discharge profiles, etc.  We have identified LFP, LTO, and NMC as candidate chemistries and are seeking vendor recommendations. Battery type and packaging are flexible so long as the other constraints of the application are met.

## Battery Management System

In operation, the BMS will be required to run from the batteries themselves and not require an external power supply, and of course be responsible for maintaining the battery cell balance and safety. The expected charge/discharge profiles are outlined in more detail in Appendix A below, but cell balancing capabilities shall be sufficient even when long periods of time exist between the battery pack being in a full state. The motor-drive system operates as a current-limited voltage supply in which the voltage and current set-points can be set remotely over CAN Bus, or the motor-drive system can be programmed to respond to battery state of charge information as needed.  The system needs to default to safe behavior in the event the CANbus communications link becomes unavailable.

## Connections

The battery system requires several different power connections with differing requirements as described below

#### Power-Converter Connection (1)

The battery connection to the motor/drive power converter must be always on and should not be disconnected in cases of low -battery-state-of-charge.  For servicing however, it is required that this connection can be turned off and galvanically isolated via a manual switch on the battery housing.  When this switch is activated, a pre-charge circuit is required to accommodate the capacitance of the motor/drive power converter.  This circuit should be fused at 50A.

#### Load Contactor-Circuits (2)

Two battery voltage connections to loads are required.  These shall be switched and galvanically isolated, each with a pre-charge capability to accommodate capacitive loads.  Switching of these circuits should be possible both by software control over CAN-bus, and autonomously in low state-of-charge conditions as described below.  Current limiting is not required, but these connections should be fused at 20A.

##### 24 Volt Supply (1)

An isolated 24V/10A supply is required that is not user switchable, but that does follow the low state-of-charge disconnect rules described below.  Switching of his 24V connection does not need to be galvanically isolated.

## Low-Voltage Disconnect

An important feature of this system is its ability to gracefully handle low energy conditions.  Occasionally at sea the conditions are calm enough that only a small amount of charging is available for long enough that loads powered from the 24V supply bring the battery state of charge to the lower end of acceptable. When this occurs, the approach used to date is to turn off all non-critical loads on the system, leaving only the battery/BMS and the motor/drive power converter active.

In wave conditions, even during the calmest conditions, 10’s of watts are typically generated, this re-charges the battery system to a suitable state of charge for the loads to be turned back on.  In tidal conditions, power generation may cease regularly, but within a period of 12 hours or less conditions suitable for power generation will occur again, allowing loads to be reestablished. The tidal system does need a brief “kick start” to resume operation, requiring approximately 100 W for a few seconds. This is manageable as long as disconnects occur at a reasonable state of charge. Additionally, implementing a low-power sleep mode during low-voltage disconnect periods could improve efficiency.

## Communications and Telemetry

These systems are CANbus based, with a single network connecting the various controllers in the system and a main supervisory/telemetry-logging Linux computer.  A simple proprietary CAN protocol is used that aims to only require each controller to stream telemetry data synchronously, and respond to a small number of commands sent asynchronously. As described previously, the motor drive has maximum voltage and current limits that can be set via CANbus, so the battery system could request various levels of charge current and voltage as needed.  In that case the system reverts to defaults if no update is given in a short timeout.  Alternatively, the motor drive can be programmed with any needed algorithm to set voltage and current limits based upon a state-of-charge or similar message from the battery system.  In every case, the system needs to revert to a safe behavior should the CANbus link become unavailable.  Ideally these behaviors can be done by the BMS, but an external micro-controller supplied by MBARI to interpret standard data from a BMS could be implemented also.

## Isolation and Environmental Monitoring

Because the battery voltages travel through several undersea cables, there is a requirement for isolation monitoring. Currently this is implemented using a commercially available unit (Bender) and simply reports the state of the insulation of the battery circuit from earth ground. No ground fault interruption is currently implemented.

## Mechanical Packaging

The battery system itself does not need to be housed/sealed to the ocean environment by the vendor. Separate housings and connectors will be developed for each application of the battery depending on depth of use and other factors. It is sufficient that the vendor guarantees safety to touch the common housing in a lab environment.

The packaging geometry becomes an important area of discussion for sub-sea use as cylindrical (or spherical) housings become much more efficient than rectangular housings at any appreciable depth.      As part of the design process, we will explore packaging options. For instance, an outer diameter limit of 11.5 inches is desirable for cylindrical housing, though this may make the system too long. Further discussion will refine the geometry based on the volume requirements for a complete package.

## Environmental Conditions

The battery system will be used on a surface buoy in the ocean, where it will be exposed to temperatures ranging from 35 to 100 degrees F.  Sunlight and resulting heating may occur, but the housing design and buoy mounting can be adjusted to mitigate this effect. When used in a sub-sea housing, the battery will have a more limited ambient temperature range 35 to 70 degrees F with no sunlight heating. The battery housing internal temperature and humidity are desirable to monitor.  Appendix A includes a power-spectral density of accelerations experienced on the buoy; note vibrations and large-scale accelerations for the tidal system are less severe than on the buoy.

## Modularity/Parallelization

Although initial use of these systems will be single pack installations, the ability to utilize one or more of these systems in parallel is attractive. In that case the ancillary features of ground-fault detection, soft-start, and low-voltage disconnect would not need to be replicated in each system.

## Safety Certifications

We are not currently seeking compliance with any specific standards for the package, as the customer-provided housing may make the system non-compliant with certain regulations. However, we would like information on specific safety standards that the vendor’s systems typically meet, as well as recommendations for minimum safety certifications. Our preliminary research suggests that IEC 61508 and UL 1973 may be suitable for functional safety.

# Appendix A

The wave and tidal energy converters have unique performance characteristics related to the average and instantaneous power generation and required system controls.

Wave energy converter: The wave-energy converter is a unique charging source in that while the average power is on the order of 10-1000 Watts, it is delivered in series of large, short duration power pulses. Figure 2 illustrates the power supplied to the battery from the wave-harvesting power-converter in rough conditions.  Simultaneously, loads on the battery system are present and are typically in the 0-1000 W range, but do not tend to oscillate as quickly.  These are not shown in Figure 2 but contribute to a relatively high frequency oscillating charge/discharge cycle.

Figure 2:  Wave-Energy Battery Power.

Figure 3 shows the computed power-spectral density of the linear accelerations experienced on the surface of the buoy in rough conditions. Additionally, shock and vibration from normal shipping and handling needs to be tolerated.

Figure 3: Acceleration PSD of surface buoy in rough conditions.

Tidal energy converter: The mean and instantaneous power generation profiles for the tidal turbine also vary with time, but to a much smaller degree than the wave energy device (Figures 4 and 5).  In most deployments the system can be expected to be generating power approximately 40% of the time or more.  Net power production begins when currents are approximately 0.75 m/s and peak, due to mechanical limitations, when currents are approximately 2.5 m/s (with the present design). The current rotor contains four blades and the resulting power generation within a given revolution of the turbine shows four cycles (Figure 2). During relatively weak currents the system goes through periods where modest power input is required in order to maintain the rotation of the rotor while maximizing its efficiency. During strong currents input power is not generally required for optimized system performance.  The result is a battery charge/discharge cycling at a relatively high frequency (~2Hz) in some conditions.

The operational range of the system spans instantaneous power values between approximately -200 W to 1800 W with time-averaged values between approximately 10 to 1700 W. Peak hydrodynamic efficiencies for the system occur at less than 100 RPM (although in torque control mode instantaneous variability on the order of 40% is possible). For this system, peak currents are considerably less than 20 A while maximum time-averaged currents are on the order of 6 A or less lasting for periods of a half hour or more under optimal (but not regularly occurring) conditions (Figure 5).

Figure 4: Examples of the torque and net power production from the turbine under two conditions. In these cases, the rotor is operating at a constant speed. The x-axis is angular position of the rotor. In these cases, the rotation rate of the rotor is between 1-1.5 Hz and due to rotational symmetry there patterns roughly nearly cosine waves except at the strongest inflow conditions.  Negative torques (Qc) indicated net power generation. The top figure shows that over most of the rotation a small negative torque is applied indicating peak instantaneous powers on the order of 110 W with averages on the order of 50 W. During brief periods, however, power is required to maintain the rotor’s velocity, resulting in a current direction reversal for the batteries.  The bottom two figures show the control torque and net power generation for currents of 2.5 m/s. During strong currents the system always generates power although intracycle variability on the order of 25 percent is observed. The mean power generation during periods of strong currents is greater than 1.5 kW and instantaneous power generation may briefly exceed 2 kW (or roughly 8 A on the 325 Vdc bus).

Figure 5: One second moving averages of power generation over different time scales. The bottom figure converts the power to current to the load dump or battery. In practice the battery should tolerate power generation on the order of at least double what is shown here, but with similar temporal characteristics. The short-time scale fluctuations in power reflect rapidly changing inflow conditions due to turbulence and the response of the controls. Note there are significant data gaps on 14-15 December and again on 16-17 December due to issues with cabled infrastructure.

# Appendix B

An overview of target technical specifications. The values in the voltage and current targets are fixed as they are a function of the power converter and environmental conditions. However, we are flexible on most of the remaining topics (except those related to protection/safety).

| Voltage, current, and SOC |  |
| --- | --- |
| Nominal voltage | 325 V |
| Min-max system voltage | 270-350 V |
| Nominal capacity | 30-35 Ah (10-12 kWh) |
| Discharge current (continuous) | 5 A |
| Discharge current (peak, < 10 s) | 30 A |
| Surge Current (< 0.5 s) | 35 A |
| Charge current (continuous) | 5 A (average), 35 A (peak) |
| Duty cycle | See Appendix A |
| SOC range | 80% |
| Maximum internal resistance | 300 mΩ |
| Battery chemistry, type, and life cycle |  |
| Chemistry | LFP, LTO, NMC (vendor recommendation requested) |
| Cell type | Vendor informed form factor |
| Cycle Life | 1000 cycles |
| Calendar life | 36 months |
| BMS |  |
| BMS supplier | Vendor recommendation |
| BMS power on method | Always on |
| Under/over Voltage Protection | Vendor defined based on system voltage |
| Over Current Protection | Vendor defined based on system current |
| Communication protocol | CAN |
| SOC accuracy | <=5% |
| How does the customer use the SOC? | Charger system can monitor and adjust charge current/voltage as needed, scheduling loads of instruments/vehicle charging |
| Will the pack be paralleled? | Desirable |
| # Thermistors | As needed |
| BMS interaction with end application (discharge) | Communication of available power and capacity. |
| BMS interaction with end application (charge) | Set charger current and voltage limit |
| Sleep/low power mode requirements | As needed to minimize power consumption during long idle states |
| Heating/Cooling needs | Passively cooled ideally |
| Environmental Conditions |  |
| Operating Temp Range | 5-40 ℃ |
| Vibration limits | See Appendix A |
| Wires and connectors |  |
| Wire lengths | 1 m |
| Connectors | Screw terminal |
| Protection |  |
| Output protection | Current Limited |
| Pre-charge circuit | Yes |
| External check for isolation? | Bender (external unit), integrate into BMS if possible |
| Ground point | Isolated DC system, battery enclosure bonded to seawater |
| Fused charger output lines | 2-3x rated current |
| Fused discharge line | 2-3x rated current |
| Enclosure | None, customer responsibility |
| Size/weight/density |  |
| Weight | As required |
| Specific energy | As required |
| Energy density | As required |
| Dimensions | As required |
| Compliance Standards |  |
| We would like information on specific safety standards that the vendor’s systems typically meet, as well as recommendations for minimum safety certifications. |  |