## Sheet1
Balanced Delta Load
Desired Line Current | 3.5 | amps
Voltage | 480 | VAC
Phase Angle Diff | 1.732
Resistance | 237.5314 | ohms
Phase Current | 2.0208 | amps
Power (each R) | 969.9769 | watts
Resistance | 270 | ohms
Variable Voltage | 480 | VAC
Phase Angle Diff | 1.732
Line Current | 3.0791 | amps
Phase Current | 1.7778 | amps
Power (each R) | 853.3333 | watts