## Slide 1: Kelp Forest Array Ground Fault Technical Review
Chad Kecy
Feb. 26 2014

## Slide 2: KFA As Deployed (Oct 2013)

## Slide 3: KFA As Deployed July 2012
KFA DC Power Supply
swFOCE DC Power Supply
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House

## Slide 4: KFA August 30, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
~200kohms to trip in ~45 minutes

## Slide 5: KFA Sept. 11, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House

## Slide 6: MBARI Sept. 12-17, 2013
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
F
M
M
M
M
M
swFOCE GF Detection Module
swFOCE DC Power Supply
M
M
F
F
KFA Central Node
1. Opened KFA CN: No shorts or visual problems
2. Independently tested GF detection module: working correctly
3. Tested for GFs on bench: OK
4. Placed KFA CN in test tank: measured 900kohms (~300uA)
(only left in tank ~10 minutes)
5. Assumption: KFA CN does not have a seawater short

## Slide 7: KFA Oct. 17, 2013 Dive #1
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
360kohms; short test
F
M
Ti Housing (Seawater Reference)

## Slide 8: KFA Oct. 17, 2013 Dive #2
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
300kohms; short test
F
M
Ti Housing (Seawater Reference)

## Slide 9: KFA Oct. 17, 2013 Dive #3
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
300kohms to 98kohms in ~10 minutes (shut off)

## Slide 10: KFA Oct. 24, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
200kohms to trip in ~60 minutes
Swapped out KFA extension cable

## Slide 11: KFA Nov. 7, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
Swapped out KFA extension cable
F
M
*
*
*
*
*
*
*
*
*
*
Added Type 44 molyKote
to female connectors
(underwater, box method)
GF (line not noted)

## Slide 12: Sheila B Dec. 5, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
*
*
*
*
*
*
*
*
*
*
Added Type 44 molyKote
to female connectors
(deck of Sheila B)
F
*
M
Cleaned every connector
Re-applied MolyKote
Tested on deck: OK
Dropped both nodes in
water: OK
5. Redeployed: OK
KFA: 1.9Mohms and rising
swFOCE: >10Mohms
Jim stayed onsite for 90 minutes

## Slide 13: KFA Dec. 11, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
GF on 300V return line (30kohms)
GF both lines (6kohms)

## Slide 14: KFA Dec. 19, 2013 Test #1
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
GF both lines (4kohms)
ON
ON
ON
OFF
OFF
OFF

## Slide 15: KFA Dec. 19, 2013 Test #2
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
GF on 300V return line (100kohms)
ON
ON
ON
OFF
OFF
OFF

## Slide 16: KFA Dec. 19, 2013 Test #3
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
swFOCE >10Mohms
ON
ON
OFF
OFF
OFF
OFF

## Slide 17: KFA Dec. 19, 2013 Test #4
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
KFA >10Mohms
ON
ON
OFF
OFF
OFF
OFF

## Slide 18: KFA Dec. 19, 2013 Test #5
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
KFA >10Mohms
ON
ON
OFF
OFF
OFF
OFF
Earth Return from Pumphouse

## Slide 19: KFA Dec. 19, 2013 Test #6
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
swFOCE >10Mohms
ON
ON
OFF
OFF
OFF
OFF
Earth Return from Pumphouse

## Slide 20: KFA Dec. 19, 2013 Test #7
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
ON
ON
OFF
OFF
OFF
Earth Return from Pumphouse
ON
GF both lines (100kohms)

## Slide 21: KFA Dec. 19, 2013 Test #8
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
ON
ON
OFF
OFF
OFF
Earth Return from Pumphouse
ON
GF on 300V return line (16kohms)

## Slide 22: KFA Dec. 19, 2013 Test #9
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
ON
ON
OFF
OFF
OFF
KFA >10Mohms
OFF

## Slide 23: KFA Dec. 19, 2013 Test #10
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
ON
ON
OFF
OFF
OFF
KFA >10Mohms
ON

## Slide 24: KFA Dec. 19, 2013 Test #11
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
ON
ON
OFF
OFF
OFF
swFOCE >10Mohms
OFF

## Slide 25: KFA Dec. 19, 2013 Test #12
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
ON
ON
OFF
OFF
swFOCE >10Mohms
OFF
ON

## Slide 26: MBARI Jan. 22, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
F
M
Test Tank Dry Side
F
M
OFF
OFF
Megger
 | 1 (V Pos) | 2 (SW Ref) | 3 (V Ret) | 12 (V Pos) | 13 (V Ret)
1 (V Pos) | X | 32.4 G | 77.5 G | 79 G | 70 G
2 (SW Ref) | X | X | 35.4 G | 36 G | 30 G
3 (V Ret) | X | X | X | 76.5 G | 71.5 G
12 (V Pos) | X | X | X | X | 62 G
13 (V Ret) | X | X | X | X | X
15 Meter SubConn GigE Cable
Cable was meggered dry in lab.

## Slide 27: MBARI Jan. 22, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
F
M
Test Tank Dry Side
F
M
OFF
OFF
Megger
15 Meter SubConn GigE Cable
 | 1 (V Pos) | 2 (SW Ref) | 3 (V Ret) | 12 (V Pos) | 13 (V Ret)
1 (V Pos) | X | 27.8 G | 56.5 G | 53 G | 50.5 G
2 (SW Ref) | X | X | 28.4 G | 28.8 G | 25 G
3 (V Ret) | X | X | X | 54 G | 51.6 G
12 (V Pos) | X | X | X | X | 43.8 G
13 (V Ret) | X | X | X | X | X
Test Tank subsea
Female end of the cable and dummy plug had type 44 MolyKote applied,
then weighted and sent to bottom of the test tank.

## Slide 28: MBARI Jan. 22, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
F
M
Test Tank Dry Side
F
M
OFF
OFF
Megger
15 Meter SubConn GigE Cable
Female end of the cable and dummy plug were placed in tank unconnected
then shaken off, and re-connected. (Simulating an underwater mating).
The mated connection was placed in the test tank for 30 minutes and then
pulled back out; meggering was done on deck.
 | 1 (V Pos) | 2 (SW Ref) | 3 (V Ret) | 12 (V Pos) | 13 (V Ret)
1 (V Pos) | X | 28.6 G | 23.8 G | 38.6 G | 34.2 G
2 (SW Ref) | X | X | 24.6 G | 33.6 G | 22 G
3 (V Ret) | X | X | X | 39.2 G | 35.6 G
12 (V Pos) | X | X | X | X | 36.6 G
13 (V Ret) | X | X | X | X | X

## Slide 29: MBARI Jan. 22, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
F
M
Test Tank Dry Side
F
M
OFF
OFF
Megger
15 Meter SubConn GigE Cable
Test Tank subsea
Female end of the cable and dummy plug were then placed back in the tank
and soaked overnight. Meggering performed the following morning.
 | 1 (V Pos) | 2 (SW Ref) | 3 (V Ret) | 12 (V Pos) | 13 (V Ret)
1 (V Pos) | X | 28.4 G | 53 G | 53.5 G | 48.8 G
2 (SW Ref) | X | X | 28.8 G | 29.2 G | 24.8 G
3 (V Ret) | X | X | X | 53.5 G | 51.5 G
12 (V Pos) | X | X | X | X | 46.6 G
13 (V Ret) | X | X | X | X | X

## Slide 30: KFA Jan 22, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
F
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
Megger
 | KFA Pos | KFA Neg | swF Pos | swF Neg | SW Ref | Armor | Earth Ref
KFA Pos | X | 2.9 G | 27 M | 0.16 M | 14 M | 0.37 M | 
KFA Neg | X | X | 1.2 G | 3.3 G | 3.2 G | 3 M | 
swF Pos | X | X | X | 15.6 M | 29.4 M | 27 M | 
swF Neg | X | X | X | X | 13 M | 1.2 M | 
SW Ref | X | X | X | X | X | 12.6 M | 
Armor | X | X | X | X | X | X | 0 ohm, 0V
Earth Ref | X | X | X | X | X | X | X
OFF
OFF

## Slide 31: KFA Jan 22, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
F
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
Megger
OFF
OFF
 | KFA Pos | KFA Neg | swF Pos | swF Neg | SW Ref | Armor | Earth Ref
KFA Pos | X | 2.8 G | 9.1 M | 0.7 M |  | 0.6 M | 0.7 M
KFA Neg | X | X | 130 G | 139 G |  | 2.6 M | 3.8 G
swF Pos | X | X | X | 20 G |  | 22 M | 19.1 M
swF Neg | X | X | X | X |  | 1.5 M | 2.3 M
SW Ref | X | X | X | X | X |  | 
Armor | X | X | X | X | X | X | 
Earth Ref | X | X | X | X | X | X | X

## Slide 32: MBARI Jan. 22, 2014 Test #5
swFOCE DC Power Supply
swFOCE GF Detection Module
F
M
Test Tank Sub Sea
Test Tank Dry Side
F
M
Dummy plug attached dry
Al Block
ON
ON
Ran for 60 minutes, GF >10Mohms
15 Meter SubConn GigE Cable

## Slide 33: MBARI Jan. 22, 2014 Test #6
swFOCE DC Power Supply
swFOCE GF Detection Module
F
Test Tank Sub Sea
Test Tank Dry Side
F
M
Connector attached dry
ON
ON
Lowered the Test Housing to bottom of tank.
Ran for 60 minutes, GF >10Mohms
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
M
Ti Test Housing
V = 375Vdc
I = 0.179A
P = 67W
15 Meter SubConn GigE Cable

## Slide 34: MBARI Jan. 23, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
F
Test Tank Sub Sea
Test Tank Dry Side
F
M
Connector attached dry
ON
ON
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
M
Ti Test Housing
V = 375Vdc
I = 0.179A
P = 67W
Left the Test Housing at the bottom of the tank overnight.
Ran for 60 minutes, GF >10Mohms
15 Meter SubConn GigE Cable

## Slide 35: MBARI Jan. 23, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
F
Test Tank Sub Sea
Test Tank Dry Side
F
M
Connector attached dry
ON
ON
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
M
Ti Test Housing
V = 375Vdc
I = 0.179A
P = 67W
Female end of the cable and dummy plug were placed in tank unconnected
then shaken off, and re-connected. (Simulating an underwater mating).
On deck, no power applied, GF > 10 Mohms
On deck, power applied, GF > 10 Mohms
In tank, power applied, GF>10 Mohms
(left in tank 60 minutes)
15 Meter SubConn GigE Cable

## Slide 36: MBARI Jan. 23, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
ON
Attached cable to swFOCE connector dry.
Ran GF test on deck.
Ran for 60 minutes, GF > 10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable

## Slide 37: MBARI Jan. 23, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
ON
Attached cable to KFA connector dry.
Ran GF test on deck.
Ran for 60 minutes, GF > 10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable

## Slide 38: MBARI Jan. 23, 2014 Test #5
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
Attached cable to KFA connector dry.
Placed CN on bottom of tank.
No power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Test Tank Sub Sea
OFF
Time | GF (ohms)
1:34 | 234k
1:35 | 260k
1:36 | 299k
1:39 | 326k
1:40 | 314k
1:50 | 163k
1:51 | 205k
1:52 | 520k
1:53 | 153k
1:54 | 182k

## Slide 39: MBARI Jan. 23, 2014 Test #6
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
Attached cable to KFA connector dry.
Placed CN on bottom of tank.
Power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Test Tank Sub Sea
ON
Time | GF (ohms)
1:55 | 300k
1:58 | 389k
2:06 | 610k
2:09 | 850k
2:10 | 108k
2:14 | 215k
2:16 | 1.1M
2:18 | 750k
2:20 | 1.4M
2:21 | 1.6M
2:30 | 1.7M
2:31 | 2.0M
2:39 | 2.4M
2:42 | 2.8M
2:45 | 3.0M

## Slide 40: MBARI Jan. 27, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
ON
Brought KFA CN back to lab and removed both endcaps and gave a visual inspection.
Hooked into earth return and ran GF test dry.
Ran for 30 minutes, GF >10Mohms

## Slide 41: MBARI Jan. 27, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
M
M
KFA Central Node
15 Meter SubConn GigE Cable
ON
Placed HV endcap into a bucket with seawater.
Hooked into earth return and ran GF test.
Ran for 30 minutes, 1.2 Mohms < GF < 9.0 Mohms
M
M
F
F

## Slide 42: MBARI Jan. 27, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
M
M
KFA Central Node
15 Meter SubConn GigE Cable
ON
Cleaned all 4 HV connectors and applied Molykote
Placed HV endcap into a bucket with seawater.
Connected KFA input.
Hooked into earth return and ran GF test.
Ran for 90 minutes, GF > 10 Mohms
M
M
F
F

## Slide 43: MBARI Jan. 27, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
M
M
KFA Central Node
15 Meter SubConn GigE Cable
ON
Cleaned all 4 HV connectors and applied Molykote
Placed HV endcap into a bucket with seawater.
Connected swFOCE input.
Hooked into earth return and ran GF test.
Ran for 60 minutes, GF > 10 Mohms
M
M
F
F

## Slide 44: MBARI Jan. 28, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
ON
Attached cable to KFA connector dry.
Ran GF test on deck.
Ran for 60 minutes, GF > 10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
** Note: CN had sat overnight in lab

## Slide 45: MBARI Jan. 28, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
ON
Attached cable to swFOCE connector dry.
Ran GF test on deck.
Ran for 60 minutes, GF >10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
** Note: No load on swFOCE at this time

## Slide 46: MBARI Jan. 28, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
Placed CN on bottom of tank.
No power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Test Tank Sub Sea
OFF
Ran for 10 minutes, GF > 10 Mohms
** Note: No load on swFOCE at this time

## Slide 47: MBARI Jan. 28, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
CN on bottom of tank.
Power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Test Tank Sub Sea
ON
Ran for 60 minutes, GF >10 Mohms
** Note: No load on swFOCE at this time

## Slide 48: MBARI Jan. 28, 2014 Test #5
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
Attached cable to KFA connector dry.
CN on deck.
Power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Time | GF (ohms)
12:51 | 8.4M
12:52 | 9.2M
12:53 | 10M
12:54 | 9.8M
12:55 | 10M
ON
** Note: CN had been in tank >60 minutes
just prior to this test.

## Slide 49: MBARI Jan. 28, 2014 Test #6
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
Blew out KFA connector with shop air (high pressure)
CN on deck.
Power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Ran for 10 minutes, GF >10 Mohms
ON

## Slide 50: MBARI Jan. 28, 2014 Test #7
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
Connector attached dry
ON
Placed CN on bottom of tank.
Power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Test Tank Sub Sea
ON
Time | GF (ohms)
1:15 | 10M
1:16 | 3.2M
1:17 | 3.7M
1:18 | 4.2M
1:19 | 4.1M
1:22 | 5.4M
1:30 | 6.4M
1:34 | 7.0M
1:44 | 8.1M
1:50 | 6.8M
2:05 | 7.2M
14:15 | 8.1M

## Slide 51: MBARI Jan. 28, 2014 Test #8
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
Attached power to swFOCE input.
Used test simulator as a load on the
swFOCE output.
Placed CN & test simulator on
bottom of tank.
Power applied.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
15 Meter SubConn GigE Cable
Test Tank Sub Sea
ON
F
Connectors attached dry
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
M
Ti Test Housing
1 Meter SubConn GigE Cable
Ran for 60 minutes, GF >10 Mohms
** Note: Load on swFOCE = 70 Watts

## Slide 52: MBARI Jan. 29, 2014
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
M
M
KFA Central Node
We suspect the KFA input connector may be bad.
Internal to the CN, we are swapping the connections of the KFA
input and swFOCE input connectors.
Meaning, the physical connector for the swFOCE input
will power the internal KFA electronics.
The KFA connector will power the swFOCE Output (external test load).
If the KFA connector is bad, then the GF should show up when
powering the external load AND no GF should appear when powering
up the KFA.
KFA Central Node Internal Electronics
Original KFA Wiring
Original swFOCE Wiring
Temporary KFA Wiring
Temporary swFOCE Wiring

## Slide 53: MBARI Jan. 29, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
J4
J3
J2
J1
F
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
M
Ti Test Housing
Ran for 30 minutes,
GF >10 Mohms
Ran Test on Deck
F
M
M
F

## Slide 54: MBARI Jan. 29, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
Ran for 30 minutes,
GF >10 Mohms
Ran Test on Deck
F
M
M
F
J4
J3
J2
J1

## Slide 55: MBARI Jan. 29, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
Ran for 30 minutes,
GF >10 Mohms
Test Tank Sub Sea
F
M
M
F
J4
J3
J2
J1

## Slide 56: MBARI Jan. 29, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
F
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
M
Ti Test Housing
Ran for 30 minutes,
GF >10 Mohms
Test Tank Sub Sea
F
M
M
F
J4
J3
J2
J1

## Slide 57: MBARI Jan. 30, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
F
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
M
Ti Test Housing
Ran for 30 minutes,
GF >10 Mohms
Test Tank Sub Sea
Soaked CN & Test Sim
in tank overnight.
F
M
M
F
J4
J3
J2
J1

## Slide 58: MBARI Jan. 30, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
Ran for 30 minutes,
GF >10 Mohms
Rewired KFA CN back
to original wiring.
On Deck
Connections made under
optimal conditions.
F
M
M
F
J4
J3
J2
J1

## Slide 59: MBARI Jan. 30, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
Ran for 5 minutes,
GF = 87kohms
Rewired KFA CN back
to original wiring.
Test Tank Sub Sea
F
M
M
F
J4
J3
J2
J1

## Slide 60: MBARI Jan. 30, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
Ran for 30 minutes,
GF >10 Mohms
Pulled back
on deck.
F
M
M
F
J4
J3
J2
J1

## Slide 61: MBARI Feb. 4-6, 2014
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
J3 - swFOCE 375V OUT
During our testing up to this point, the likely
culprit appeared to be one or more of the
Subconn high voltage connectors.
During a series of tests, I rotated the housing
in the crane such that I could lower the CN
into the tank one connector at a time.

## Slide 62: MBARI Feb. 4-6, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF = 1.6 Mohms
J4
J3
J2
J1
Test Tank Sub Sea

## Slide 63: MBARI Feb. 4-6, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF >10 Mohms
J4
J3
J2
J1
Test Tank Sub Sea

## Slide 64: MBARI Feb. 4-6, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF >10 Mohms
On Deck
J4
J3
J2
J1

## Slide 65: MBARI Feb. 4-6, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF = 1.1 Mohms
Test Tank Sub Sea
J4
J3
J2
J1

## Slide 66: MBARI Feb. 4-6, 2014 Test #5
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF > 10 Mohms
Test Tank Sub Sea
J4
J3
J2
J1

## Slide 67: MBARI Feb. 4-6, 2014 Test #6
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF > 10 Mohms
J4
J3
J2
J1
Test Tank Sub Sea

## Slide 68: MBARI Feb. 4-6, 2014 Test #7
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF > 10 Mohms
J4
J3
J2
J1
Test Tank Sub Sea

## Slide 69: MBARI Feb. 4-6, 2014 Test #8
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF = 3.7 Mohms
J4
J3
J2
J1
Test Tank Sub Sea

## Slide 70: MBARI Feb. 4-6, 2014 Test #9
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF >10 Mohms
J4
J3
J2
J1
On Deck

## Slide 71: MBARI Feb. 4-6, 2014 Test #10
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF = 1.7 Mohms
Test Tank Sub Sea
J4
J3
J2
J1

## Slide 72: MBARI Feb. 4-6, 2014 Test #11
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF = 1.6 Mohms
Test Tank Sub Sea
J4
J3
J2
J1

## Slide 73: MBARI Feb. 4-6, 2014 Test #12
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF = 1.6 Mohms
Test Tank Sub Sea
J4
J3
J2
J1

## Slide 74: MBARI Feb. 4-6, 2014 Test #13
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF = 1.6 Mohms
Test Tank Sub Sea
J4
J3
J2
J1

## Slide 75: MBARI Feb. 4-6, 2014 Test #14
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
KFA Central Node
J3 - swFOCE 375V OUT
GF >10 Mohms
Test Tank Sub Sea
J4
J3
J2
J1

## Slide 76: MBARI Feb. 10, 2014
Replaced J4
Analysis of “bad” J4 revealed no obvious
defects or problems.

## Slide 77: MBARI Feb. 11, 2014
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
J1 - KFA 300V IN
J4 - KFA 300V OUT
J2 - swFOCE 375V IN
F
F
M
M
KFA Central Node
KFA Central Node Internal Electronics
J3 - swFOCE 375V OUT
F
M
M
F
J4
J3
J2
J1
Ran for 60 minutes,
GF >10 Mohms

## Slide 78: MBARI Feb. 12, 2014 Test #1
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
Ran for 30 minutes,
GF >10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
F
F
M
M
F
F
M
M
2 Meter SubConn GigE Cable

## Slide 79: MBARI Feb. 12, 2014 Test #2
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
Ran for 30 minutes,
GF >10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
F
F
M
M
F
F
M
M
2 Meter SubConn GigE Cable
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
F
M

## Slide 80: MBARI Feb. 12, 2014 Test #3
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
Ran for 30 minutes,
GF >10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
F
F
M
M
F
F
M
M
2 Meter SubConn GigE Cable
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
F
M
KFA DC Power Supply
KFA GF Detection Module
F
M
ON
ON
15 Meter SubConn GigE Cable

## Slide 81: MBARI Feb. 12, 2014 Test #4
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
Ran for 3 hours
GF >10 Mohms
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
F
F
M
M
F
F
M
M
2 Meter SubConn GigE Cable
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
F
M
KFA DC Power Supply
KFA GF Detection Module
F
M
ON
ON
15 Meter SubConn GigE Cable

## Slide 82: MBARI Feb. 13, 2014
swFOCE DC Power Supply
swFOCE GF Detection Module
Test Tank Dry Side
F
M
ON
15 Meter SubConn GigE Cable
ON
Soaked overnight
with power OFF.
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
M
M
M
M
KFA Central Node
F
F
M
M
F
F
M
M
2 Meter SubConn GigE Cable
Vicor Maxi
Pwr Res
375V:48V
600W
50ohms
160W
1A (50W)
F
M
KFA DC Power Supply
KFA GF Detection Module
F
M
ON
ON
15 Meter SubConn GigE Cable
KFA GF = 2.1M
swFOCE GF =8.0M

## Slide 83
Peter Walz and I noticed the GFs only
appeared when the whip:BH connection
was subsea, not the whip:whip sections.

## Slide 84
Proposed solution: Replace all HV
bulkhead connectors with Penetrator
style whips.
This also reduces the total number of
subsea connections.

## Slide 85: Proposed Interconnections
KFA MicroNode
KFA Central Node
swFOCE Central Node
375V In
375V Out
300V Out
300V In
300V Out
48V Out
48V Out
2 Meters
2 Meters
2 Meters
2 Meters
2 Meters
2 Meters
2 Meters
Need 15 Meter sections
to individual swFOCE
experiments

## Slide 86: Megger readings on KFA Tether
 | KFA Pos | KFA Neg | swFOCE Pos | swFOCE Neg | SW Ref | Earth Ref | K-Tube | Inner Jacket | Armor | Outer Jacket
KFA Pos | X | 5.1 G | 3.2 G | 1.8 G | 605 M | 13.5 M | 1.4 G | 90 M | 14.3 M | 1.9 G
KFA Neg | X | X | 9.5 G | 6.9 G | 3.8 G | 6.3 G | 7.1 G | 3.0 G | 5.9 G | 1.7 G
swFOCE Pos | X | X | X | 5.9 G | 3.5 G | 3.3 G | 5.3 G | 2.1 G | 3.0 G | 1.9 G
swFOCE Neg | X | X | X | X | 2.7 G | 1.9 G | 3.4 G | 1.3 G | 1.9 G | 2.3 G
SW Ref | X | X | X | X | X | 680 M | 2.5 G | 645 M | 660 M | 2.1 G
Earth Ref | X | X | X | X | X | X | 1.4 G | 79 M | 0,0 | 2.0 G
K-Tube | X | X | X | X | X | X | X | 1.2 G | 1.2 G | 2.2 G
Inner Jacket | X | X | X | X | X | X | X | X | 62 M | 1.7 G
Armor | X | X | X | X | X | X | X | X | X | 1.7 G
Outer Jacket | X | X | X | X | X | X | X | X | X | X

## Slide 87
Outer Jacket
Armor
Inner Jacket
Mylar
Tape

## Slide 88
Outer Jacket
Inner Jacket
Armor
K-Tube
swFOCE Pos
swFOCE Neg
KFA Pos
KFA Neg
Seawater Ref
Earth Ref
62M
14.3M
90M
79M
0,0
13.5M