## Slide 1: Kelp Forest Array Ground Fault Technical Review
Chad Kecy
Dec. 19 2013

## Slide 2: KFA Deployed (Oct 2013)

## Slide 3: KFA As Deployed July 2012
KFA DC Power Supply
swFOCE DC Power Supply
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House

## Slide 4: KFA August 30, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
~200kohms to trip in ~45 minutes

## Slide 5: KFA Sept. 11, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House

## Slide 6: MBARI Sept. 12-17, 2013
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
F
F
F
F
F
M
M
M
M
M
swFOCE GF Detection Module
swFOCE DC Power Supply
M
M
F
F
KFA Central Node
1. Opened KFA CN: No shorts or visual problems
2. Independently tested GF detection module: working correctly
3. Tested for GFs on bench: OK
4. Placed KFA CN in test tank: measured 900kohms (~300uA)
(only left in tank ~10 minutes)
5. Assumption: KFA CN does not have a seawater short

## Slide 7: KFA Oct. 17, 2013 Dive #1
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
360kohms; short test
F
M
Ti Housing (Seawater Reference)

## Slide 8: KFA Oct. 17, 2013 Dive #2
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
Tether (200m)
5 x 14AWG
F
F
F
F
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
300kohms; short test
F
M
Ti Housing (Seawater Reference)

## Slide 9: KFA Oct. 17, 2013 Dive #3
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
300kohms to 98kohms in ~10 minutes (shut off)

## Slide 10: KFA Oct. 24, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
200kohms to trip in ~60 minutes
Swapped out KFA extension cable

## Slide 11: KFA Nov. 7, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
GF on 300V return line
Swapped out KFA extension cable
F
M
*
*
*
*
*
*
*
*
*
*
Added Type 44 molyKote
to female connectors
(underwater, box method)
GF (line not noted)

## Slide 12: Sheila B Dec. 5, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
*
*
*
*
*
*
*
*
*
*
Added Type 44 molyKote
to female connectors
(deck of Sheila B)
F
*
M
Cleaned every connector
Re-applied MolyKote
Tested on deck: OK
Dropped both nodes in
water: OK
5. Redeployed: OK
KFA: 1.9Mohms and rising
swFOCE: >10Mohms
Jim stayed onsite for 90 minutes

## Slide 13: KFA Dec. 11, 2013
KFA DC Power Supply
swFOCE DC Power Supply
KFA GF Detection Module
swFOCE GF Detection Module
Diver Lockout Box
KFA Micro Node
KFA Central Node
KFA 300V IN
KFA 300V OUT
swFOCE 375V IN
swFOCE 375V OUT
Tether (200m)
5 x 14AWG
F
F
F
F
F
F
F
F
M
M
M
M
M
M
M
M
KFA 300V OUT
swFOCE 375V OUT
Sub Sea
Hopkins Pump House
F
M
F
M
GF on 300V return line (30kohms)
GF both lines (6kohms)