## 6017 - GF#1
ADAM-6017 | Ground Fault #1
IP Address:
Pin | Signal Name | Destination | Signal Range | Description
VIN0+ | GP1 | Vicor Board #1 | 0-5V | Differential signal indicating a ground fault on Vicor Board #1
VIN0- | GN1 | Vicor Board #1 | 0V
VIN1+ | GP2 | Vicor Board #1 | 0-5V | Differential signal indicating a ground fault on Vicor Board #2
VIN1- | GN2 | Vicor Board #1 | 0V
VIN2+ | GP3 | Vicor Board #2 | 0-5V | Differential signal indicating a ground fault on Vicor Board #3
VIN2- | GN3 | Vicor Board #2 | 0V
VIN3+ | GP4 | Vicor Board #2 | 0-5V | Differential signal indicating a ground fault on Vicor Board #4
VIN3- | GN4 | Vicor Board #2 | 0V
VIN4+ | GND | Vicor Board #3 | 0V | Unused
VIN4- | GND | Vicor Board #3 | 0V | Unused
VIN5+ | GND | Vicor Board #3 | 0V | Unused
VIN5- | GND | Vicor Board #3 | 0V | Unused
VIN6+ | GND | Vicor Board #4 | 0V | Unused
VIN6- | GND | Vicor Board #4 | 0V | Unused
VIN7+ | GND | Vicor Board #4 | 0V | Unused
VIN7- | GND | Vicor Board #4 | 0V | Unused
DO0 | GF_CON_3 | Vicor Board #3 | Digital; 5V logic | Activates Ground Fault Monitor on Vicor Board #3
DO1 | GF_CON_4 | Vicor Board #4 | Digital; 5V logic | Activates Ground Fault Monitor on Vicor Board #3

## 6017 - Analog #1
ADAM-6017 | Analog #1
IP Address:
Pin | Signal Name | Destination | Signal Range | Description
VIN0+ | IL1 | Vicor Board #1 | 0-5V | Differential signal indicating load current on Vicor #1
VIN0- | GND | Vicor Board #1
VIN1+ | IL2 | Vicor Board #2 | 0-5V | Differential signal indicating load current on Vicor #2
VIN1- | GND | Vicor Board #2
VIN2+ | IL3 | Vicor Board #3 | 0-5V | Differential signal indicating load current on Vicor #3
VIN2- | GND | Vicor Board #3
VIN3+ | IL4 | Vicor Board #4 | 0-5V | Differential signal indicating load current on Vicor #4
VIN3- | GND | Vicor Board #4
VIN4+ | TH1_POS | Vicor Board #1 | 0-5V | Differential signal indicating temperature of Vicor #1
VIN4- | GND | Vicor Board #1
VIN5+ | TH2_POS | Vicor Board #2 | 0-5V | Differential signal indicating temperature of Vicor #2
VIN5- | GND | Vicor Board #2
VIN6+ | TH3_POS | Vicor Board #3 | 0-5V | Differential signal indicating temperature of Vicor #3
VIN6- | GND | Vicor Board #3
VIN7+ | TH4_POS | Vicor Board #4 | 0-5V | Differential signal indicating temperature of Vicor #4
VIN7- | GND | Vicor Board #4
DO0 | GF_CON_1 | Vicor Board #1 | Digital; 5V logic | Activates Ground Fault Monitor on Vicor Board #1
DO1 | GF_CON_2 | Vicor Board #2 | Digital; 5V logic | Activates Ground Fault Monitor on Vicor Board #2

## 6017 - GF #2
ADAM-6017 | Ground Fault #2
IP Address:
Pin | Signal Name | Destination | Signal Range | Description
VIN0+ | GP5 | Vicor Board #5 | 0-5V | Differential signal indicating a ground fault on Vicor Board #5
VIN0- | GN5 | Vicor Board #5 | 0V
VIN1+ | GP6 | Vicor Board #6 | 0-5V | Differential signal indicating a ground fault on Vicor Board #6
VIN1- | GN6 | Vicor Board #6 | 0V
VIN2+ | GND | Vicor Board #6 | 0V
VIN2- | GND | Vicor Board #6 | 0V
VIN3+ | GND | Vicor Board #6 | 0V
VIN3- | GND | Vicor Board #6 | 0V
VIN4+
VIN4-
VIN5+
VIN5-
VIN6+
VIN6-
VIN7+
VIN7-
DO0 | GF_CON_5 | Vicor Board #5 | Digital; 5V logic | Activates Ground Fault Monitor on Vicor Board #5
DO1 | GF_CON_6 | Vicor Board #6 | Digital; 5V logic | Activates Ground Fault Monitor on Vicor Board #6

## 6017 - Analog #2
ADAM-6017 | Analog #1
IP Address:
Pin | Signal Name | Destination | Signal Range | Description
VIN0+ | IL5 | Vicor Board #5 | 0-5V | Differential signal indicating load current on Vicor #5
VIN0- | GND | Vicor Board #5
VIN1+ | IL6 | Vicor Board #6 | 0-5V | Differential signal indicating load current on Vicor #6
VIN1- | GND | Vicor Board #6
VIN2+
VIN2-
VIN3+
VIN3-
VIN4+ | TH5_POS | Vicor Board #5 | 0-5V | Differential signal indicating temperature of Vicor #5
VIN4- | GND | Vicor Board #5
VIN5+ | TH6_POS | Vicor Board #6 | 0-5V | Differential signal indicating temperature of Vicor #6
VIN5- | GND | Vicor Board #6
VIN6+
VIN6-
VIN7+
VIN7-
DO0
DO1

## 6066 - Cont #1
ADAM-6066 | Control #1
IP Address:
Pin | Signal Name | Destination | Signal Range | Description
DI 0 | STAT1 | Vicor Board #1 | Digital; 5V logic | Power ON status for Vicor #1
DI 1 | STAT2 | Vicor Board #2 | Digital; 5V logic | Power ON status for Vicor #2
DI 2 | STAT3 | Vicor Board #3 | Digital; 5V logic | Power ON status for Vicor #3
DI 3 | STAT4 | Vicor Board #4 | Digital; 5V logic | Power ON status for Vicor #4
DI 4 | STAT5 | Vicor Board #5 | Digital; 5V logic | Power ON status for Vicor #5
DI 5 | STAT6 | Vicor Board #6 | Digital; 5V logic | Power ON status for Vicor #6
RL 0+ | CTRL1 | Vicor Board #1 | 0-12V | Activation voltage for Vicor #1
RL 0- | GND | Patch Board #1 | 0V | Source voltage for relays
RL 1+ | CTRL2 | Vicor Board #2 | 0-12V | Activation voltage for Vicor #2
RL 1- | GND | Patch Board #1 | 0V | Source voltage for relays
RL 2+ | CTRL3 | Vicor Board #3 | 0-12V | Activation voltage for Vicor #3
RL 2- | GND | Patch Board #1 | 0V | Source voltage for relays
RL 3+ | CTRL4 | Vicor Board #4 | 0-12V | Activation voltage for Vicor #4
RL 3- | GND | Patch Board #1 | 0V | Source voltage for relays
RL 4+ | CTRL5 | Vicor Board #5 | 0-12V | Activation voltage for Vicor #5
RL 4- | GND | Patch Board #1 | 0V | Source voltage for relays
RL 5+
RL 5-

## 6066 - Cont #2
ADAM-6066 | Control #2
IP Address:
Pin | Signal Name | Destination | Signal Range | Description
DI 0
DI 1
DI 2
DI 3
DI 4
DI 5
RL 0+ | VPOS | Patch Board #1 | +12V | Source voltage for Aux Nodes
RL 0- | 12V_INSTR_1 | Aux Node #1 | 0-12V | Power for Aux Node #1
RL 1+ | VPOS | Patch Board #1 | +12V | Source voltage for Aux Nodes
RL 1- | 12V_INSTR_2 | Aux Node #2 | 0-12V | Power for Aux Node #2
RL 2+ | VPOS | Patch Board #1 | +12V | Source voltage for Aux Nodes
RL 2- | 12V_INSTR_3 | Aux Node #3 | 0-12V | Power for Aux Node #3
RL 3+ | VPOS | Patch Board #1 | +12V | Source voltage for Aux Nodes
RL 3- | 12V_INSTR_4 | Aux Node #4 | 0-12V | Power for Aux Node #4
RL 4+ | 300V_CON1 | 300V Dist Board | 12V | Activation for HV Node
RL 4- | 300V_CON2 | 300V Dist Board | 12V | Activation for HV Node
RL 5+
RL 5-