## Central Node
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
FAN_01_STATE | Digital | Off | On | N/A | N/A | N/A
FAN_02_STATE | Digital | Off | On | N/A | N/A | N/A
VICOR_01_STATE | Digital | Off | On | N/A | N/A | N/A
VICOR_02_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_01_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_02_STATE | Digital | Off | On | N/A | N/A | N/A
48V_READY | Digital | Ready | Not | N/A | N/A | N/A
375V_READY | Digital | Ready | Not | N/A | N/A | N/A
H2O_SENSE_01 | Digital | Normal | H2O Leak | N/A | N/A | N/A
H2O_SENSE_02 | Digital | Normal | H2O Leak | N/A | N/A | N/A
375V_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 425 | Volts
375V_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 5 | Amps
VICOR_TEMP_01 | Analog | N/A | N/A | 0 to 3.0V | 0 to 90 | degC
VICOR_TEMP_02 | Analog | N/A | N/A | 0 to 3.0V | 0 to 90 | degC
VICOR_TEMP_03 | Analog | N/A | N/A | 0 to 3.0V | 0 to 90 | degC
HEATSINK_TEMP | Analog | N/A | N/A | 0 to 3.0V | 0 to 90 | degC
48V_01_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 12.5 | Amps
48V_01_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
48V_02_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 12.5 | Amps
48V_02_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
24V_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 3.125 | Amps
24V_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 30 | Volts
3.3V_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 4 | Amps
3.3V_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 3.6 | Volts
AMB_HUM | Analog | N/A | N/A | 0 to 5.0V | 0 to 100 | %RH
AMB_TEMP | Analog | N/A | N/A | 0 to 5.0V | -40 to 80 | degC
GF_CURR | Analog | N/A | N/A | 0 to 5.0V | -1 to +1 | mA

## MEH #1
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
Motor #1 Current | Analog | N/A | N/A | 0 to 5.0V | -800 to 800 | RPM |  | AD1
Motor #2 Current | Analog | N/A | N/A | 0 to 5.0V | -800 to 800 | RPM |  | AD2
Ambient Temperature | Analog | N/A | N/A | 0 to 5.0V | -40 to 80 | degC |  | AD3
Ambient Humidity | Analog | N/A | N/A | 0 to 5.0V | 0 to 100 | %RH |  | AD4
H2O Sense #1 | Analog | N/A | N/A | 0 to 5.0V | N/A | on/off |  | AD5
H2O Sense #2 | Analog | N/A | N/A | 0 to 5.0V | N/A | on/off |  | AD6

## MEH #2
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
Motor #1 Current | Analog | N/A | N/A | 0 to 5.0V | -800 to 800 | RPM |  | AD1
Motor #2 Current | Analog | N/A | N/A | 0 to 5.0V | -800 to 800 | RPM |  | AD2
Ambient Temperature | Analog | N/A | N/A | 0 to 5.0V | -40 to 80 | degC |  | AD3
Ambient Humidity | Analog | N/A | N/A | 0 to 5.0V | 0 to 100 | %RH |  | AD4
H2O Sense #1 | Analog | N/A | N/A | 0 to 5.0V | N/A | on/off |  | AD5
H2O Sense #2 | Analog | N/A | N/A | 0 to 5.0V | N/A | on/off |  | AD6

## Gateway Node #1
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
NODE_1_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_2_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_3_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_4_STATE | Digital | Off | On | N/A | N/A | N/A
H2O_ALARM | Digital | H2O Leak | Normal | N/A | N/A | N/A
ENVR_ALARM | Digital | Alarm | Normal | N/A | N/A | N/A
NODE_1_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
NODE_2_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
NODE_3_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
NODE_4_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
GF_CURR | Analog | N/A | N/A | 0 to 1.8V | -1 to +1 | mA
48V_VOLT | Analog | N/A | N/A | 0 to 1.8V | 0 to 60 | Volts
48V_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 6 | Amps
AMB_TEMP | Analog | N/A | N/A | SPI | -25 to 85 | degC
AMB_HUM | Analog | N/A | N/A | SPI | 10 to 90 | %RH
VICOR_TEMP | Analog | N/A | N/A | SPI | -200 to 700 | degC

## Gateway Node #2
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
NODE_1_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_2_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_3_STATE | Digital | Off | On | N/A | N/A | N/A
NODE_4_STATE | Digital | Off | On | N/A | N/A | N/A
H2O_ALARM | Digital | H2O Leak | Normal | N/A | N/A | N/A
ENVR_ALARM | Digital | Alarm | Normal | N/A | N/A | N/A
NODE_1_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
NODE_2_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
NODE_3_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
NODE_4_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 2 | Amps
GF_CURR | Analog | N/A | N/A | 0 to 1.8V | -1 to +1 | mA
48V_VOLT | Analog | N/A | N/A | 0 to 1.8V | 0 to 60 | Volts
48V_CURR | Analog | N/A | N/A | 0 to 1.8V | 0 to 6 | Amps
AMB_TEMP | Analog | N/A | N/A | SPI | -25 to 85 | degC
AMB_HUM | Analog | N/A | N/A | SPI | 10 to 90 | %RH
VICOR_TEMP | Analog | N/A | N/A | SPI | -200 to 700 | degC

## Sensor Node #1
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA

## Sensor Node #2
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA
|  | 0 | 1 | Full Scale | Signal | Units | Sample Rate
INSTR_1_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_2_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_3_STATE | Digital | Off | On | N/A | N/A | N/A
INSTR_4_STATE | Digital | Off | On | N/A | N/A | N/A
CONFIG_BIT_x | Digital
INSTR_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
INSTR_VOLT | Analog | N/A | N/A | 0 to 3.0V | 0 to 60 | Volts
INSTR_1_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_2_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_3_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 2 | Amps
INSTR_4_CURR | Analog | N/A | N/A | 0 to 3.0V | 0 to 6 | Amps
4_20MA_VOLT | Analog | N/A | N/A | 0 to 3.0V | 4 to 22 | mA