## Slide 1: Shallow Water FOCE Kelp Forest Array Shore Side High Voltage Distribution
Chad Kecy
June xx, 2012

## Slide 2: What is the KFA Cabled Observatory?
Underwater observatory
8 Science ports + 2 Expansion ports
  4 Primary: 48v, 24v, 24v, 24v [10/100 Ethernet]
  4 Secondary: 12v, 12v, 12v, 12v [Serial]
  1 High Voltage: 300v [Gigabit Ethernet]
  1 swFOCE Pass Through: 375v [Gigabit Ethernet]

## Slide 3: KFA Deployment Site

## Slide 5: Shore Side Functionality
Generate HV for KFA (300V @ 3A)
Generate HV for swFOCE (375V @ 6A)
Ethernet Comms for KFA (Gigabit)
Ethernet Comms for swFOCE (Gigabit)
Generate and deliver enriched seawater to swFOCE
Publish and store scientific data

## Slide 6: Pumphouse Components
Electronics Rack
Enriched
Seawater
Chamber
208VAC 20A
375V/300V/Fibers
Control
Signals
Tether
ESW Tubing
T1 Line

## Slide 8: High Voltage Schematic
See OrCad schematic
208VAC 20A available in pumphouse
UPS + Isolation xfmr
4 individually breakered 120VAC outputs
375v / 300v Generation
Ground fault protection
Physical lock out box

## Slide 9: TrippLite SU5000RT3U UPS System
208Vac, 24A Input
208/120Vac Output
3500W Output
8min at full load
20min at half load
120Vac output isolated
3U Power Module
2U Isolation Transformer
2U Battery Module

## Slide 10: Sorensen XG600-2.8 HV Power Supply
0-600Vdc , 2.8A
1.05kW available at 375Vdc
Running two in parallel for 2.1kW at 375Vdc
Interlock shutoff

## Slide 11: KFA Power Supply

## Slide 12: Ground Fault Assembly
SSC800-25
SS Relay
GigaVAC GX12
Relay
Bender IRDH275
Ground Fault Monitor
IXYS
Diode
From XG600-2.8
HV Power Supplies
To High Voltage
Lockout Box
Seawater
Ground
375Vdc
To PS
Interlock

## Slide 13: High Voltage Lockout Box
HBLDS Disconnect Switch
HBLDS Disconnect Switch
KFA
Tether
To swFOCE
GF Module
To KFA
GF Module
Fiber connections not shown

## Slide 14: Diver Safety
The KFA Observatory will be de-energized while divers are in the vicinity.
The divers will have possession of the key to the high voltage lockout box while diving.

## Slide 15: High Voltage Safety Features
Safety switch to remove 208VAC from entire rack enclosure.
20A 208VAC circuit breaker at main bldg panel
Over/under voltage and over current protection at the XG600-2.8 DC Power Supply
Seawater ground fault detection with built in circuit breaker functionality
Physical lockout box for diver safety

## Slide 16: GF Module Relays
Gigavec HV DC Contactor
750V, 20 A
13,500 life cycles
Release time = 20 ms
<$150 each
Crydom SSC
800V, 25A
Ron = 60mohm
0.3 mA max leakage current
Max turn off time = 1.5 msec
$109

## Slide 17: GF Module GFCI Module
Bender IRDH275 Module