# Medium Voltage Converter Modbus Interface

### Project: SW-FOCE – Project 901219
Revision – 1.0
Date: 12/06/2013

The software interface to the Medium Voltage Converter board is Modbus over RS-232 -- http://modbus.org/docs/Modbus_Application_Protocol_V1_1b3.pdf -- to two serial-over-ethernet ports that are implemented via an on-board dual-port MatchPort.  The intent is that one serial port will be used for logging of engineering parameters, and one will be used for control and display via the GUI or similar interface; but in fact these two ports are serviced identically, and they can be used in whatever manner the system builder deems appropriate.  By default, these Modbus ports run at 115200 baud; but this can be changed via the debug port.  This document specifies the Modbus resources that are exposed via this interface.

## Modbus Coils

| Coil | Name | Default | Description |
| --- | --- | --- | --- |
| 1 | VICOR_01 | 0 | Turn on/off Vicor #1 |
| 2 | VICOR_02 | 0 | Turn on/off Vicor #2 |
| 3 | FOCE_01 | 0 | Open/close relay to FOCE #1 |
| 4 | FOCE_02 | 0 | Open/close relay to FOCE #2 |
| 5 | BLINKY_DEBUG | 1 | Use blinky LED in debug mode |
| 6 | BLINKY_STATE | 0 | Blinky LED state – only active if BLINKY_DEBUG is 0 |

### Power Notes

- Each power circuit (01, 02) has a Vicor to generate 48V followed by a relay to connect that power to the SW-FOCE unit.

- 375V_RDY (See register 0x14) must be 1 before attempting to turn on either Vicor.  If not true, a command to set either Vicor coil will return an error.

- Both 375V_RDY and 48V_RDY must be 1 before attempting to turn on either FOCE.  If not true, a command to close either FOCE relay will return an error.

### LED Notes

- The LED can operate in two modes:  Debug mode or Program mode

- In Debug mode (BLINKY_DEBUG = 1) the LED stays lit until the first valid Modbus message arrives on either port.  After that, it blinks.

- In Program mode (BLINKY_DEBUG = 0), the LED is controlled by BLINKY_STATE

## Modbus Registers

| Register | Name | Default | Description |
| --- | --- | --- | --- |
| 0x10 | SERIAL_NUM | 1 | Board serial number. Can be set via DEBUG port |
| 0x11 | SW_REVISION | 0x100 | Software revision. MSB = major rev, LSB = minor rev |
| 0x14 | SYS_STATUS |  | Bit 0 = FAN01_STATE, Bit 1 = FAN02_STATE Bit2 = VICOR01_STATE, Bit 3 = VICOR02_STATE Bit 4 = FOCE01_STATE, Bit 5 = FOCE02_STATE Bit 6 = 48V_RDY, Bit 7 = 375V_RDY |
| 0x15 | FAN_CTRL | 0x0b | See Fan Notes |
| 0x16 | FAN_TMP01_SETPT | 30 | Degrees C – Fan Notes |
| 0x17 | FAN_TMP02_SETPT | 30 | Degrees C – Fan Notes |
| 0x18 | GF_CTRL | 0x00 | See Ground Fault Notes |
| 0x19 | GF_RESULT |  | Range -1 to +1 ma = 0 to 65535 counts |
| 0x1a | GF_SAMP_PERIOD | 10 |  |
| 0x1b | GF_IGNORE_SAMPS | 2 |  |
| 0x1c | H2O_SENSE | 0 | Bit 0 = H2O_SENSE_01, Bit 1 = H2O_SENSE_02 |
|  | ADC Conversions |  |  |
| 0x20 | 375V_VOLT |  | Range 0-425V. V = (cnts-148)/154.057 |
| 0x21 | 375V_CURR |  | Range 0-5.0A. A = cnts/13107 |
| 0x22 | VICOR_01_TEMP |  | Range 0-90C. C = cnts/655.35 |
| 0x23 | VICOR_02_TEMP |  | Range 0-90C. C = cnts/655.35 |
| 0x24 | VICOR_03_TEMP |  | Range 0-90C. C = cnts/655.35 |
| 0x25 | HEATSINK_TEMP |  | Range 0-90C. C = cnts/655.35 |
| 0x26 | 48V_01_VOLT |  | Range 0-60V. V= cnts/1092.27 |
| 0x27 | 48V_01_CURR |  | Range 0-12.5A. A= cnts/5242.88 |
| 0x28 | 48V_02_VOLT |  | Range 0-60V. V= cnts/1092.27 |
| 0x29 | 48V_02_CURR |  | Range 0-12.5A. A= cnts/5242.88 |
| 0x2a | 24V_VOLT |  | Range 0-30V. V= cnts/2184.33 |
| 0x2b | 24V_CURR |  | Range 0-3.125A. A= cnts/19662.77 |
| 0x2c | 3.3V_VOLT |  | Range 0-3.6V. V= cnts/18204.44 |
| 0x2d | 3.3V_CURR |  | Range 0-4.0A. A= cnts/16384 |
| 0x2e | AMB_HUMID |  | Range 0-100%. %rh = cnt/349.5 – 37.7 |
| 0x2f | AMB_TEMP |  | Range -40 to +80C. |
|  | ADC Control |  |  |
| 0x30 | ADC_NUM_AVG | 1 | Number of A/D samples to average |
| 0x31 | ADC_AVG_MS | 1 | Time in milliseconds between each sample |

### Fan Notes

FAN_CTRL consists of two 2-bit fields.  The field consisting of bits 0,1 controls Fan 01, and the field consisting of bits 2,3 controls Fan 02.  For each field:

00 = Fan Off
01 = Fan On
10 = Fan controlled by FAN_TMP01_SETPT
11 = Fan controlled by FAN_TMP02_SETPT

In the case of 10 or 11, if the temperature for the corresponding Vicor is below the set point, the fan is off.  If the temperature is above the setpoint, the fan is on.  There is some hysteresis (TBD).

### Ground Fault Notes

A Ground Fault conversion is started by setting the GF_CTRL register with a value consisting of exactly one bit on.  Any attempt to set multiple bits will result in an error.  The bits are defined as:

Bit 0: 48V_01  - High side of the first 48V Vicor
Bit 1: 48V_01_RET – Low side of the first 48V Vicor
Bit 2: 48V_02  - High side of the second 48V Vicor
Bit 3: 48V_02_RET – Low side of the second 48V Vicor
Bit 4: TEST_GF – High side of GF test circuit
Bit 5: TEST_GF_RET -- Low side of GF test circuit
Bits 6, 7: Must be 0

When GF_CTRL is set with a non-zero value, the system will sample and average the ground fault circuit, one sample every GF_SAMP_PERIOD milliseconds.  The first GF_IGNORE_SAMPS samples are discarded, to allow the circuit some time to settle.  A maximum of (TBD) samples will be averaged.

When the user/application subsequently reads the GF_RESULT register, the averaged result is returned.  This has the side effect of discontinuing the sampling and resetting GF_CTRL to 00.

### A/D Notes

Reading any one (or multiple) A/D register in the range of 0x20 to 0x2f causes the system to read the documented A/D channel(s).  The channel(s) is(are) read ADC_NUM_AVG times, once every ADC_AVG_MS milliseconds; and the average of those samples is returned.

Note that ADC_NUM_AVG and ADC_AVG_MS must have the property that the product of these two registers is less than or equal to 250 ms.  Any attempt to set these registers so that the product exceeds 250 ms will result in an error.

## Misc Notes

The PIC firmware that implements this spec is single-threaded.  This is possible because Modbus is a synchronous, command-response protocol.  Therefore, whenever a command is received on either serial port, the command is processed and a response is sent before the other serial port is serviced.

## Debug Port

There is a 3rd serial port, the debug port.  This runs a simple menu-driven interface at 9600 baud, N81.  This interface lets you set baud rates, serial number, LED state, etc.  As soon as any valid Modbus message is received on either of the two operational serial ports, the debug port becomes inactive.