# Medium Voltage Converter Modbus Interface

### Project: SW-FOCE – Project 901219
Revision – 1.4
Date: 2/3/2015

The software interface to the Medium Voltage Converter board is Modbus over RS-232 -- http://modbus.org/docs/Modbus_Application_Protocol_V1_1b3.pdf -- to two serial-over-ethernet ports that are implemented via an on-board dual-port MatchPort.  The intent was that one serial port would be used for logging of engineering parameters, and one will be used for control and display via the GUI or similar interface.  It was subsequently learned that the freemodbus library is single threaded, so at this point, only the first serial port on the MatchPort is used for servicing Modbus messages.

By default, the Modbus port runs at 115200 baud; but this can be changed via the debug port.  This document specifies the Modbus resources that are exposed via this interface.

## Modbus Coils

| Coil | Name | Default | Description |
| --- | --- | --- | --- |
| 1 | VICOR_01 | 0 | Turn on/off Vicor #1 |
| 2 | VICOR_02 | 0 | Turn on/off Vicor #2 |
| 3 | FOCE_01 | 0 | Open/close relay to FOCE #1 |
| 4 | FOCE_02 | 0 | Open/close relay to FOCE #2 |
| 5 | FAN_01 | 1 | Turn on/off Fan #1 |
| 6 | FAN_02 | 1 | Turn on/off Fan #2 |
| 7 | BLINKY_DEBUG | 1 | Use blinky LED in debug mode |
| 8 | BLINKY_STATE | 0 | Blinky LED state – only active if BLINKY_DEBUG is 0 |

### Power Notes

- Each power circuit (01, 02) has a Vicor to generate 48V followed by a relay to connect that power to the SW-FOCE unit.

- The  Vicor must be turned on for a minimum of 500 ms (?)  before you can close the corresponding FOCE relay.  Otherwise, the command to close the FOCE relay will return an error.

### LED Notes

- The LED can operate in two modes:  Debug mode or Program mode

- In Debug mode (BLINKY_DEBUG = 1) the LED stays lit until the first valid Modbus message arrives on either port.  After that, it blinks.

- In Program mode (BLINKY_DEBUG = 0), the LED is controlled by BLINKY_STATE

## Modbus Registers

| Register | Name | Default | Description |
| --- | --- | --- | --- |
| 0x10 | SERIAL_NUM | 1 | Board serial number. Can be set via DEBUG port |
| 0x11 | SW_REVISION | 0x100 | Software revision. MSB = major rev, LSB = minor rev |
| 0x12 | SYS_STATUS |  | Bit 0 = FAN01_STATE, Bit 1 = FAN02_STATE Bit2 = VICOR01_STATE, Bit 3 = VICOR02_STATE Bit 4 = FOCE01_STATE, Bit 5 = FOCE02_STATE |
| 0x13 | GF_NUM_SAMPS | 10 | Number of samples to average for each GF channel |
| 0x14 | GF_SAMP_PERIOD | 100 | GF Sample period in ms (rounds to nearest 10ms) |
| 0x15 | GF_IGNORE_SAMPS | 10 | Number of initial samples to ignore for each channel |
| 0x16 | GF_CTRL | 1 | See Ground Fault Notes |
| 0x17 | GF_SEQ | 1 | Sequence number for GF tests. See GF Notes |
| 0x18 | GF_CHAN | 0 | Current channel being sampled |
| 0x19 | GF_48V_01 | 0 | Result of last test of GF_48V_01 channel |
| 0x1a | GF_48V_01_RET | 0 | Result of last test of GF_48V_01_RET channel |
| 0x1b | GF_48V_02 | 0 | Result of last test of GF_48V_02 channel |
| 0x1c | GF_48V_02_RET | 0 | Result of last test of GF_48V_02_RET channel |
| 0x1d | GF_TEST | 0 | Result of last test of GF_TEST channel. Only active if bit 1 of GF_CTRL register is set |
| 0x1e | GF_TEST_RET | 0 | Result of last test of GF_TEST_RET channel. Only active if bit 1 of GF_CTRL register is set |
| 0x1f | H2O_SENSE | 0 | Bit 0 = H2O_SENSE_01, Bit 1 = H2O_SENSE_02 |
|  | ADC Conversions |  |  |
| 0x20 | VICOR_01_TEMP |  | Range 0-100C. C = cnts/655.35 |
| 0x21 | VICOR_02_TEMP |  | Range 0-100C. C = cnts/655.35 |
| 0x22 | VICOR_03_TEMP |  | Range 0-100C. C = cnts/655.35 |
| 0x23 | HEATSINK_TEMP |  | Range 0-100C. C = cnts/655.35 |
| 0x24 | 48V_01_CURR |  | Range 0-12.5A. A= cnts/5242.88 |
| 0x25 | 48V_01_VOLT |  | Range 0-60V. V= cnts/1092.27 |
| 0x26 | 48V_02_CURR |  | Range 0-12.5A. A= cnts/5242.88 |
| 0x27 | 48V_02_VOLT |  | Range 0-60V. V= cnts/1092.27 |
| 0x28 | 24V_CURR |  | Range 0-3.33A. A= cnts/19680.5 |
| 0x29 | 24V_VOLT |  | Range 0-30V. V= cnts/2184.33 |
| 0x2a | 3.3V_CURR |  | Range 0-2.0A. A= cnts/32768. |
| 0x2b | 3.3V_VOLT |  | Range 0-3.6V. V= cnts/18204.44 |
| 0x2c | AMB_HUMID |  | Range 0-100%. %rh = cnt/349.5 – 37.7 |
| 0x2d | AMB_TEMP |  | Range -40 to +80C. |
|  | ADC Control |  |  |
| 0x30 | ADC_NUM_AVG | 1 | Number of A/D samples to average |
| 0x31 | ADC_AVG_MS | 1 | Time in milliseconds between each sample |

### Ground Fault Notes

The ground fault channels are continuously sampled in the background, and is controlled by the 2  LSB bits of the GF_CTRL register, as follows:

00: Ground fault monitoring off
01: Check normal channels only (GF_48V_01 through GF_48V_02_RET)
10: Check test channels only (GF_TEST and GF_TEST_RET)
11: Check all 6 GF channels

The default value of GF_CTRL is 01, which checks the GF channels 0-3 (GF_48V_01 through GF_48V_02_RET)

The user can get the results of the last GF test for any channel by reading the corresponding GF register.  The GF_SEQ register can be used to discover when a new set of (normally 4) ground fault results is available.  That way, you can avoid reading the same result over and over.

For each ground fault channel, the firmware performs the following sequence of actions:

- Select the appropriate ground fault channel

- Ignore the first GF_IGNORE_SAMPS samples, to allow the analog circuitry to stabilize after selecting the new channel.

- Sample the ground fault channel every GF_SAMP_PERIOD milliseconds, for a total GF_NUM_SAMPS samples.  Note that GF_SAMP_PERIOD will be rounded to the nearest 10ms, and has minimum value of 10ms.

- Average the samples, and store the average A/D count in the corresponding result register

- Repeat for all ground fault channels.  After all are done, increment the GF_SEQ and start over with the first channel (normally GF_48V_01)

### A/D Notes

Reading any one (or multiple) A/D register in the range of 0x20 to 0x2d causes the system to read the documented A/D channel(s).  The channel(s) is (are) read ADC_NUM_AVG times, once every ADC_AVG_MS milliseconds; and the average of those samples is returned.

Note that ADC_NUM_AVG and ADC_AVG_MS must have the property that the product of these two registers is less than or equal to 250 ms.  Any attempt to set these registers so that the product exceeds 250 ms will result in an error.

## Misc Notes

The PIC firmware that implements this spec is single-threaded.  This is possible because Modbus is a synchronous, command-response protocol.  Therefore, whenever a command is received on either serial port, the command is processed and a response is sent before the other serial port is serviced.

No longer relevant, since only one serial port is serviced.

## Debug Port

There is a 3rd serial port, the debug port.  This runs a simple menu-driven interface at 9600 baud, N81.  This interface lets you set baud rates, serial number, LED state, etc.  As soon as any valid Modbus message is received on either of the two operational serial ports, the debug port becomes inactive.