## AWG DC Resistances
| DC Resistance | DC Resistance | DC Resistance
AWG | ohms/1000ft | ohms/ft | ohms/meter
26 | 67.3 | 0.0673 | 0.020513
24 | 42.1 | 0.0421 | 0.012832
22 | 26.6 | 0.0266 | 0.0081077
20 | 16.6 | 0.0166 | 0.0050597
18 | 10.5 | 0.0105 | 0.0032004
16 | 6.59 | 0.00659 | 0.0020086
14 | 4.14 | 0.00414 | 0.0012619
12 | 2.6 | 0.0026 | 0.00079248
10 | 1.64 | 0.00164 | 0.00049987

## nsFOCE Power Losses
Shore | Units | Description
410 | volts | Shore Voltage
14 | awg | Conductor size in tether
2 | pairs | # of conductor pairs
1500 | feet | Length to Micronode
0.00414 | Ω/foot | DC resistance per foot
5.25 | Amps | Maximum current
6.21 | Ω | DC resistance to Micronode
32.6025 | volts | Max voltage drop in tether
377.3975 | volts | Voltage at the Micronode
20 | awg | Conductor size in -11FG cable
3 | pairs | # of conductor pairs
82 | feet | Length to Distribution Node
0.0166 | Ω/foot | DC resistance per foot
1.25 | Amps | Maximum current
0.90747 | Ω | DC resistance to Dist Node
1.1343 | volts | Max voltage drop in -11FG cable
376.2632 | volts | Voltage at Distribution Node
20 | awg | Conductor size in -10FG cable
2 | pairs | # of conductor pairs
82 | feet | Length to Chamber Node
0.0166 | Ω/foot | DC resistance per foot
1.2 | Amps | Maximum current
1.3612 | Ω | DC resistance to Chamber Node
1.6334 | volts | Max voltage drop in -10FG cable
374.6297 | volts | Voltage at Chamber Node
35.3703 | volts | Total (max) voltage losses

## Tether Testing
volts | amps | watts | ohms | volts | amps | watts | volts | ohms | amps | watts
prog | meas | calc | prog | meas | meas | calc | calc | calc | meas | calc
Vsource | Isource | Psource | Rload | Vload | Iload | Pload | Vtether | Rtether | Itether | Ptether | Notes
400.2 | 0.1 | 40.02 | 4000 | 400.2 | 0.1 | 40.02 | 0 | 0 | 0.1 | 0
400.2 | 0.19 | 76.038 | 2000 | 399.85 | 0.19 | 75.9715 | 0.35 | 1.8421 | 0.19 | 0.0665
400.2 | 0.39 | 156.078 | 1000 | 399.01 | 0.39 | 155.6139 | 1.19 | 3.0513 | 0.39 | 0.4641
400.2 | 0.49 | 196.098 | 800 | 398.59 | 0.49 | 195.3091 | 1.61 | 3.2857 | 0.49 | 0.7889
400.2 | 0.99 | 396.198 | 400 | 396.5 | 0.99 | 392.535 | 3.7 | 3.7374 | 0.99 | 3.663
400.2 | 1.18 | 472.236 | 333 | 395.7 | 1.18 | 466.926 | 4.5 | 3.8136 | 1.18 | 5.31
400.2 | 1.38 | 552.276 | 286 | 394.85 | 1.38 | 544.893 | 5.35 | 3.8768 | 1.38 | 7.383
400.2 | 1.57 | 628.314 | 250 | 394.05 | 1.57 | 618.6585 | 6.15 | 3.9172 | 1.57 | 9.6555
400.2 | 1.76 | 704.352 | 222 | 393.23 | 1.76 | 692.0848 | 6.97 | 3.9602 | 1.76 | 12.2672
400.2 | 1.95 | 780.39 | 200 | 392.42 | 1.95 | 765.219 | 7.78 | 3.9897 | 1.95 | 15.171
400.2 | 2.15 | 860.43 | 182 | 391.63 | 2.15 | 842.0045 | 8.57 | 3.986 | 2.15 | 18.4255
400.2 | 2.33 | 932.466 | 167 | 390.83 | 2.33 | 910.6339 | 9.37 | 4.0215 | 2.33 | 21.8321
400.2 | 2.52 | 1008.504 | 154 | 390.03 | 2.52 | 982.8756 | 10.17 | 4.0357 | 2.52 | 25.6284
400.2 | 2.71 | 1084.542 | 143 | 389.24 | 2.71 | 1054.8404 | 10.96 | 4.0443 | 2.71 | 29.7016
400.2 | 2.8 | 1120.56 | 138 | 388.86 | 2.8 | 1088.808 | 11.34 | 4.05 | 2.8 | 31.752
400.2 | 3 | 1200.6 |  | 387.9 | 3 | 1163.7 | 12.3 | 4.1 | 3 | 36.9
400.2 | 3.2 | 1280.64 |  | 387.08 | 3.2 | 1238.656 | 13.12 | 4.1 | 3.2 | 41.984
400.2 | 3.4 | 1360.68 |  | 386.26 | 3.4 | 1313.284 | 13.94 | 4.1 | 3.4 | 47.396
400.2 | 3.6 | 1440.72 |  | 385.44 | 3.6 | 1387.584 | 14.76 | 4.1 | 3.6 | 53.136
400.2 | 3.8 | 1520.76 |  | 384.62 | 3.8 | 1461.556 | 15.58 | 4.1 | 3.8 | 59.204
400.2 | 4 | 1600.8 |  | 383.8 | 4 | 1535.2 | 16.4 | 4.1 | 4 | 65.6
400.2 | 4.2 | 1680.84 |  | 382.56 | 4.2 | 1606.752 | 17.64 | 4.2 | 4.2 | 74.088
400.2 | 4.4 | 1760.88 |  | 381.72 | 4.4 | 1679.568 | 18.48 | 4.2 | 4.4 | 81.312
400.2 | 4.6 | 1840.92 |  | 380.88 | 4.6 | 1752.048 | 19.32 | 4.2 | 4.6 | 88.872
400.2 | 4.8 | 1920.96 |  | 380.04 | 4.8 | 1824.192 | 20.16 | 4.2 | 4.8 | 96.768
400.2 | 5 | 2001 |  | 379.2 | 5 | 1896 | 21 | 4.2 | 5 | 105
400.2 | 5.2 | 2081.04 |  | 378.36 | 5.2 | 1967.472 | 21.84 | 4.2 | 5.2 | 113.568
400.2 | 5.4 | 2161.08 |  | 377.52 | 5.4 | 2038.608 | 22.68 | 4.2 | 5.4 | 122.472
400.2 | 5.6 | 2241.12 |  | 376.68 | 5.6 | 2109.408 | 23.52 | 4.2 | 5.6 | 131.712