Procedure for powering up and down the KFA & swFOCE systems.

See the attached schematic for more details.

** The diver lockout switches should only be turned on/off with the power off. **

To turn ON the KFA system:

- Verify the KFA diver lockout switch is in the ON position.

- Turn on the Low Voltage Power Supply (LVPS).

  - The green LED on LVPS should be on.

- Turn on the KFA Ground Fault Module (GFM).

  - You should hear the electromechanical relays click on.

  - The Bender unit will begin a self-test.

  - After ~60 seconds, the GFM should indicate >10Mohms

- Turn on the KFA High Voltage Power Supply (HVPS).

  - The HVPS will come on with the output disabled.

- Depress the Output Enable button on the KFA HVPS.

  - The Voltage display should read ~324Vdc. 400Vdc

  - Once the KFA reaches steady state, the current should read ~240ma. 50ma.

To turn OFF the KFA System:

- Depress the Output Enable button the KFA HVPS.

  - The output voltage and current should both go to zero.

- Turn off the KFA HVPS.

Note: The LVPS supplies 12Vdc to both Ground Fault Modules. It needs to stay on if either of the systems are energized.

To turn ON the swFOCE system:

- Verify the swFOCE diver lockout switch is in the ON position.

- Turn on the Low Voltage Power Supply (LVPS).

  - The green LED on LVPS should be on.

- Turn on the swFOCE Ground Fault Module (GFM).

  - You should hear the electromechanical relays click on.

  - The Bender unit will begin a self-test.

  - After ~60 seconds, the GFM should indicate >10Mohms

- Turn on the swFOCE High Voltage Power Supply (HVPS).

  - The HVPS will come on with the output disabled.

- Depress the Output Enable button on the swFOCE HVPS.

  - The Voltage display should read ~400Vdc.

  - Once the swFOCE reaches steady state, the current should read ~240ma.

    - Current level will change depending on deployed equipment

To turn OFF the swFOCE System:

- Depress the Output Enable button the swFOCE HVPS.

  - The output voltage and current should both go to zero.

- Turn off the swFOCE HVPS.

Note: The LVPS supplies 12Vdc to both Ground Fault Modules. It needs to stay on if either of the systems are energized.