## Sheet1
| Sys | Sys | ISO | Thrust
| 24 | 12 | 24 | 48
Wago Stack | 0.5
Valve | 3
Crydom Relay | 0.015
Crydom Relay | 0.015
Digi Ser Server |  | 0.5
SBE5T Pump |  | 1.8
SBE5T Pump |  | 1.8
SBE43 CTD |  | 0.1
SBE43 CTD |  | 0.1
Durafet |  |  | 0.1
Durafet |  |  | 0.1
Durafet |  |  | 0.1
Durafet |  |  | 0.1
Thruster |  |  |  | 6.25
Low DC Watts | 84.72 | 51.6 | 9.6 | 300
375V Wattage | 105.9 | 64.5 | 12 | 375
Vicor Rated Watts | 150w | 75w | 75w | 600w
| Micro | Micro | Micro | Maxi
375 Watts | 557.4 | Watts
375 Current | 1.4864 | Amps

## Sheet2
Wattage
Static | 92
Static + Valve | 182
State + Thruster (Max) | 692
State + Valve + Thruster (Max) | 782
| W/Cham | # chamb | Tot Watts | Volt | Amps
| 600 | 4 | 2400 | 400 | 6

## Sheet3
| ohms/1000Ft | ohms/Ft | ohms/Meter |  | 1 way | Round Trip
| 20 degC | 20 degC | 20 degC | Length | Total R | Total R | Source | Load | Loss | Load V
AWG | ohms | ohms | ohms | Meters | ohms | ohms | volts | amps | volts | volts
12 | 1.588 | 0.001588 | 0.00521 | 200 | 1.042 | 2.084 | 400 | 6 | 12.5039 | 387.4961
14 | 2.525 | 0.002525 | 0.0082841 | 200 | 1.6568 | 3.3136 | 400 | 6 | 19.8819 | 380.1181 | X
16 | 4.016 | 0.004016 | 0.013176 | 200 | 2.6352 | 5.2703 | 400 | 6 | 31.622 | 368.378
18 | 6.385 | 0.006385 | 0.020948 | 200 | 4.1896 | 8.3793 | 400 | 6 | 50.2756 | 349.7244
20 | 10.15 | 0.01015 | 0.033301 | 200 | 6.6601 | 13.3202 | 400 | 6 | 79.9213 | 320.0787
22 | 16.14 | 0.01614 | 0.052953 | 200 | 10.5906 | 21.1811 | 400 | 6 | 127.0866 | 272.9134
Output of micronode to chambers/cn | [5 empty] | 3 pairs
20 | 10.15 | 0.01015 | 0.033301 | 20 | 0.66601 | 0.44401 | 380 | 6 | 2.664 | 377.336