## Wago Stack
PN# | Func | Mod# | Tank#
750-352 | Coupler | 1 | ALL
750-468 | Analog In | 3 | 1
750-468 | Analog In | 9 | 2
750-468 | Analog In | 12 | 3
750-468 | Analog In | 15 | 4
750-468 | Analog In | 18 | 5
750-468 | Analog In | 21 | 6
750-468 | Analog In | 24 | 7
750-468 | Analog In | 27 | 8
750-468 | Analog In | 30 | 9
750-468 | Analog In | 34 | 10
750-468 | Analog In | 37 | 11
750-468 | Analog In | 40 | 12
750-468 | Analog In | 43 | 13
750-468 | Analog In | 46 | 14
750-468 | Analog In | 49 | 15
750-468 | Analog In | 52 | 16
750-460 | RTD In | 4 | 1
750-460 | RTD In | 10 | 2
750-460 | RTD In | 13 | 3
750-460 | RTD In | 16 | 4
750-460 | RTD In | 19 | 5
750-460 | RTD In | 22 | 6
750-460 | RTD In | 25 | 7
750-460 | RTD In | 28 | 8
750-460 | RTD In | 31 | 9
750-460 | RTD In | 35 | 10
750-460 | RTD In | 38 | 11
750-460 | RTD In | 41 | 12
750-460 | RTD In | 44 | 13
750-460 | RTD In | 47 | 14
750-460 | RTD In | 50 | 15
750-460 | RTD In | 53 | 16
750-559 | Analog Out | 2 | 1
750-559 | Analog Out | 8 | 2
750-559 | Analog Out | 11 | 3
750-559 | Analog Out | 14 | 4
750-559 | Analog Out | 17 | 5
750-559 | Analog Out | 20 | 6
750-559 | Analog Out | 23 | 7
750-559 | Analog Out | 26 | 8
750-559 | Analog Out | 29 | 9
750-559 | Analog Out | 33 | 10
750-559 | Analog Out | 36 | 11
750-559 | Analog Out | 39 | 12
750-559 | Analog Out | 42 | 13
750-559 | Analog Out | 45 | 14
750-559 | Analog Out | 48 | 15
750-559 | Analog Out | 51 | 16
750-612 | 24V Input | 5 | ALL
750-1504 | Dig Out | 6 | 1-8
750-1504 | Dig Out | 32 | 9-16
750-600 | Term | 7 | ALL

## SW Assignments
Wago | Description | Mod | Tank | Chan | Wago Signal | Register | Signal Name | Signal Description
750-352 | Ethernet TCP/IP Fieldbus coupler
750-468 | 4-Chan Analog In 0-10Vdc | 3 | 1 | 1 | AI1 | 0 | C1_PH_SIG | Conditioning Tank pH
|  | 3 | 1 | 2 | AI2 | 1 | C1_O2_SIG | Conditioning Tank O2
|  | 3 | 1 | 3 | AI3 | 2 | E1_PH_SIG | Experimental Tank pH
|  | 3 | 1 | 4 | AI4 | 3 | E1_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 9 | 2 | 1 | AI1 | 4 | C2_PH_SIG | Conditioning Tank pH
|  | 9 | 2 | 2 | AI2 | 5 | C2_O2_SIG | Conditioning Tank O2
|  | 9 | 2 | 3 | AI3 | 6 | E2_PH_SIG | Experimental Tank pH
|  | 9 | 2 | 4 | AI4 | 7 | E2_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 12 | 3 | 1 | AI1 | 8 | C3_PH_SIG | Conditioning Tank pH
|  | 12 | 3 | 2 | AI2 | 9 | C3_O2_SIG | Conditioning Tank O2
|  | 12 | 3 | 3 | AI3 | 10 | E3_PH_SIG | Experimental Tank pH
|  | 12 | 3 | 4 | AI4 | 11 | E3_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 15 | 4 | 1 | AI1 | 12 | C4_PH_SIG | Conditioning Tank pH
|  | 15 | 4 | 2 | AI2 | 13 | C4_O2_SIG | Conditioning Tank O2
|  | 15 | 4 | 3 | AI3 | 14 | E4_PH_SIG | Experimental Tank pH
|  | 15 | 4 | 4 | AI4 | 15 | E4_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 18 | 5 | 1 | AI1 | 16 | C5_PH_SIG | Conditioning Tank pH
|  | 18 | 5 | 2 | AI2 | 17 | C5_O2_SIG | Conditioning Tank O2
|  | 18 | 5 | 3 | AI3 | 18 | E5_PH_SIG | Experimental Tank pH
|  | 18 | 5 | 4 | AI4 | 19 | E5_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 21 | 6 | 1 | AI1 | 20 | C6_PH_SIG | Conditioning Tank pH
|  | 21 | 6 | 2 | AI2 | 21 | C6_O2_SIG | Conditioning Tank O2
|  | 21 | 6 | 3 | AI3 | 22 | E6_PH_SIG | Experimental Tank pH
|  | 21 | 6 | 4 | AI4 | 23 | E6_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 24 | 7 | 1 | AI1 | 24 | C7_PH_SIG | Conditioning Tank pH
|  | 24 | 7 | 2 | AI2 | 25 | C7_O2_SIG | Conditioning Tank O2
|  | 24 | 7 | 3 | AI3 | 26 | E7_PH_SIG | Experimental Tank pH
|  | 24 | 7 | 4 | AI4 | 27 | E7_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 27 | 8 | 1 | AI1 | 28 | C8_PH_SIG | Conditioning Tank pH
|  | 27 | 8 | 2 | AI2 | 29 | C8_O2_SIG | Conditioning Tank O2
|  | 27 | 8 | 3 | AI3 | 30 | E8_PH_SIG | Experimental Tank pH
|  | 27 | 8 | 4 | AI4 | 31 | E8_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 30 | 9 | 1 | AI1 | 32 | C9_PH_SIG | Conditioning Tank pH
|  | 30 | 9 | 2 | AI2 | 33 | C9_O2_SIG | Conditioning Tank O2
|  | 30 | 9 | 3 | AI3 | 34 | E9_PH_SIG | Experimental Tank pH
|  | 30 | 9 | 4 | AI4 | 35 | E9_02_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 34 | 10 | 1 | AI1 | 36 | C10_PH_SIG | Conditioning Tank pH
|  | 34 | 10 | 2 | AI2 | 37 | C10_O2_SIG | Conditioning Tank O2
|  | 34 | 10 | 3 | AI3 | 38 | E10_PH_SIG | Experimental Tank pH
|  | 34 | 10 | 4 | AI4 | 39 | E10_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 37 | 11 | 1 | AI1 | 40 | C11_PH_SIG | Conditioning Tank pH
|  | 37 | 11 | 2 | AI2 | 41 | C11_O2_SIG | Conditioning Tank O2
|  | 37 | 11 | 3 | AI3 | 42 | E11_PH_SIG | Experimental Tank pH
|  | 37 | 11 | 4 | AI4 | 43 | E11_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 40 | 12 | 1 | AI1 | 44 | C12_PH_SIG | Conditioning Tank pH
|  | 40 | 12 | 2 | AI2 | 45 | C12_O2_SIG | Conditioning Tank O2
|  | 40 | 12 | 3 | AI3 | 46 | E12_PH_SIG | Experimental Tank pH
|  | 40 | 12 | 4 | AI4 | 47 | E12_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 43 | 13 | 1 | AI1 | 48 | C13_PH_SIG | Conditioning Tank pH
|  | 43 | 13 | 2 | AI2 | 49 | C13_O2_SIG | Conditioning Tank O2
|  | 43 | 13 | 3 | AI3 | 50 | E13_PH_SIG | Experimental Tank pH
|  | 43 | 13 | 4 | AI4 | 51 | E13_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 46 | 14 | 1 | AI1 | 52 | C14_PH_SIG | Conditioning Tank pH
|  | 46 | 14 | 2 | AI2 | 53 | C14_O2_SIG | Conditioning Tank O2
|  | 46 | 14 | 3 | AI3 | 54 | E14_PH_SIG | Experimental Tank pH
|  | 46 | 14 | 4 | AI4 | 55 | E14_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 49 | 15 | 1 | AI1 | 56 | C15_PH_SIG | Conditioning Tank pH
|  | 49 | 15 | 2 | AI2 | 57 | C15_O2_SIG | Conditioning Tank O2
|  | 49 | 15 | 3 | AI3 | 58 | E15_PH_SIG | Experimental Tank pH
|  | 49 | 15 | 4 | AI4 | 59 | E15_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 52 | 16 | 1 | AI1 | 60 | C16_PH_SIG | Conditioning Tank pH
|  | 52 | 16 | 2 | AI2 | 61 | C16_O2_SIG | Conditioning Tank O2
|  | 52 | 16 | 3 | AI3 | 62 | E16_PH_SIG | Experimental Tank pH
|  | 52 | 16 | 4 | AI4 | 63 | E16_O2_SIG | Experimental Tank O2
750-460 | 4-Chan Analog In RTD | 4 | 1 | 1 | R1+/R1- | 64 | C1_T_SIG | Conditioning Tank Temperature
|  | 4 | 1 | 2 | R2+/R2- | 65 | E1_T_SIG | Experimental Tank Temperature
|  | 4 | 1 | 3 | R3+/R3- | 66 | B1_T_SIG | Water Bath Temperature
|  | 4 | 1 | 4 | R4+/R4- | 67
750-460 | 4-Chan Analog In RTD | 10 | 2 | 1 | R1+/R1- | 68 | C2_T_SIG | Conditioning Tank Temperature
|  | 10 | 2 | 2 | R2+/R2- | 69 | E2_T_SIG | Experimental Tank Temperature
|  | 10 | 2 | 3 | R3+/R3- | 70 | B2_T_SIG | Water Bath Temperature
|  | 10 | 2 | 4 | R4+/R4- | 71
750-460 | 4-Chan Analog In RTD | 13 | 3 | 1 | R1+/R1- | 72 | C3_T_SIG | Conditioning Tank Temperature
|  | 13 | 3 | 2 | R2+/R2- | 73 | E3_T_SIG | Experimental Tank Temperature
|  | 13 | 3 | 3 | R3+/R3- | 74 | B3_T_SIG | Water Bath Temperature
|  | 13 | 3 | 4 | R4+/R4- | 75
750-460 | 4-Chan Analog In RTD | 16 | 4 | 1 | R1+/R1- | 76 | C4_T_SIG | Conditioning Tank Temperature
|  | 16 | 4 | 2 | R2+/R2- | 77 | E4_T_SIG | Experimental Tank Temperature
|  | 16 | 4 | 3 | R3+/R3- | 78 | B4_T_SIG | Water Bath Temperature
|  | 16 | 4 | 4 | R4+/R4- | 79
750-460 | 4-Chan Analog In RTD | 19 | 5 | 1 | R1+/R1- | 80 | C5_T_SIG | Conditioning Tank Temperature
|  | 19 | 5 | 2 | R2+/R2- | 81 | E5_T_SIG | Experimental Tank Temperature
|  | 19 | 5 | 3 | R3+/R3- | 82 | B5_T_SIG | Water Bath Temperature
|  | 19 | 5 | 4 | R4+/R4- | 83
750-460 | 4-Chan Analog In RTD | 22 | 6 | 1 | R1+/R1- | 84 | C6_T_SIG | Conditioning Tank Temperature
|  | 22 | 6 | 2 | R2+/R2- | 85 | E6_T_SIG | Experimental Tank Temperature
|  | 22 | 6 | 3 | R3+/R3- | 86 | B6_T_SIG | Water Bath Temperature
|  | 22 | 6 | 4 | R4+/R4- | 87
750-460 | 4-Chan Analog In RTD | 25 | 7 | 1 | R1+/R1- | 88 | C7_T_SIG | Conditioning Tank Temperature
|  | 25 | 7 | 2 | R2+/R2- | 89 | E7_T_SIG | Experimental Tank Temperature
|  | 25 | 7 | 3 | R3+/R3- | 90 | B7_T_SIG | Water Bath Temperature
|  | 25 | 7 | 4 | R4+/R4- | 91
750-460 | 4-Chan Analog In RTD | 28 | 8 | 1 | R1+/R1- | 92 | C8_T_SIG | Conditioning Tank Temperature
|  | 28 | 8 | 2 | R2+/R2- | 93 | E8_T_SIG | Experimental Tank Temperature
|  | 28 | 8 | 3 | R3+/R3- | 94 | B8_T_SIG | Water Bath Temperature
|  | 28 | 8 | 4 | R4+/R4- | 95
750-460 | 4-Chan Analog In RTD | 31 | 9 | 1 | R1+/R1- | 96 | C9_T_SIG | Conditioning Tank Temperature
|  | 31 | 9 | 2 | R2+/R2- | 97 | E9_T_SIG | Experimental Tank Temperature
|  | 31 | 9 | 3 | R3+/R3- | 98 | B9_T_SIG | Water Bath Temperature
|  | 31 | 9 | 4 | R4+/R4- | 99
750-460 | 4-Chan Analog In RTD | 35 | 10 | 1 | R1+/R1- | 100 | C10_T_SIG | Conditioning Tank Temperature
|  | 35 | 10 | 2 | R2+/R2- | 101 | E10_T_SIG | Experimental Tank Temperature
|  | 35 | 10 | 3 | R3+/R3- | 102 | B10_T_SIG | Water Bath Temperature
|  | 35 | 10 | 4 | R4+/R4- | 103
750-460 | 4-Chan Analog In RTD | 38 | 11 | 1 | R1+/R1- | 104 | C11_T_SIG | Conditioning Tank Temperature
|  | 38 | 11 | 2 | R2+/R2- | 105 | E11_T_SIG | Experimental Tank Temperature
|  | 38 | 11 | 3 | R3+/R3- | 106 | B11_T_SIG | Water Bath Temperature
|  | 38 | 11 | 4 | R4+/R4- | 107
750-460 | 4-Chan Analog In RTD | 41 | 12 | 1 | R1+/R1- | 108 | C12_T_SIG | Conditioning Tank Temperature
|  | 41 | 12 | 2 | R2+/R2- | 109 | E12_T_SIG | Experimental Tank Temperature
|  | 41 | 12 | 3 | R3+/R3- | 110 | B12_T_SIG | Water Bath Temperature
|  | 41 | 12 | 4 | R4+/R4- | 111
750-460 | 4-Chan Analog In RTD | 44 | 13 | 1 | R1+/R1- | 112 | C13_T_SIG | Conditioning Tank Temperature
|  | 44 | 13 | 2 | R2+/R2- | 113 | E13_T_SIG | Experimental Tank Temperature
|  | 44 | 13 | 3 | R3+/R3- | 114 | B13_T_SIG | Water Bath Temperature
|  | 44 | 13 | 4 | R4+/R4- | 115
750-460 | 4-Chan Analog In RTD | 47 | 14 | 1 | R1+/R1- | 116 | C14_T_SIG | Conditioning Tank Temperature
|  | 47 | 14 | 2 | R2+/R2- | 117 | E14_T_SIG | Experimental Tank Temperature
|  | 47 | 14 | 3 | R3+/R3- | 118 | B14_T_SIG | Water Bath Temperature
|  | 47 | 14 | 4 | R4+/R4- | 119
750-460 | 4-Chan Analog In RTD | 50 | 15 | 1 | R1+/R1- | 120 | C15_T_SIG | Conditioning Tank Temperature
|  | 50 | 15 | 2 | R2+/R2- | 121 | E15_T_SIG | Experimental Tank Temperature
|  | 50 | 15 | 3 | R3+/R3- | 122 | B15_T_SIG | Water Bath Temperature
|  | 50 | 15 | 4 | R4+/R4- | 123
750-460 | 4-Chan Analog In RTD | 53 | 16 | 1 | R1+/R1- | 124 | C16_T_SIG | Conditioning Tank Temperature
|  | 53 | 16 | 2 | R2+/R2- | 125 | E16_T_SIG | Experimental Tank Temperature
|  | 53 | 16 | 3 | R3+/R3- | 126 | B16_T_SIG | Water Bath Temperature
|  | 53 | 16 | 4 | R4+/R4- | 127
750-559 | 4-Chan Analog Out 0-10Vdc | 2 | 1 | 1 | AO1 | 512 | V1_CO2_CONT | CO2 Gas Valve Control
|  | 2 | 1 | 2 | AO2 | 513 | V1_O2_CONT | O2 Gas Valve Control
|  | 2 | 1 | 3 | AO3 | 514 | V1_N2_CONT | N2 Gas Valve Control
|  | 2 | 1 | 4 | AO4 | 515
750-559 | 4-Chan Analog Out 0-10Vdc | 8 | 2 | 1 | AO1 | 516 | V2_CO2_CONT | CO2 Gas Valve Control
|  | 8 | 2 | 2 | AO2 | 517 | V2_O2_CONT | O2 Gas Valve Control
|  | 8 | 2 | 3 | AO3 | 518 | V2_N2_CONT | N2 Gas Valve Control
|  | 8 | 2 | 4 | AO4 | 519
750-559 | 4-Chan Analog Out 0-10Vdc | 11 | 3 | 1 | AO1 | 520 | V3_CO2_CONT | CO2 Gas Valve Control
|  | 11 | 3 | 2 | AO2 | 521 | V3_O2_CONT | O2 Gas Valve Control
|  | 11 | 3 | 3 | AO3 | 522 | V3_N2_CONT | N2 Gas Valve Control
|  | 11 | 3 | 4 | AO4 | 523
750-559 | 4-Chan Analog Out 0-10Vdc | 14 | 4 | 1 | AO1 | 524 | V4_CO2_CONT | CO2 Gas Valve Control
|  | 14 | 4 | 2 | AO2 | 525 | V4_O2_CONT | O2 Gas Valve Control
|  | 14 | 4 | 3 | AO3 | 526 | V4_N2_CONT | N2 Gas Valve Control
|  | 14 | 4 | 4 | AO4 | 527
750-559 | 4-Chan Analog Out 0-10Vdc | 17 | 5 | 1 | AO1 | 528 | V5_CO2_CONT | CO2 Gas Valve Control
|  | 17 | 5 | 2 | AO2 | 529 | V5_O2_CONT | O2 Gas Valve Control
|  | 17 | 5 | 3 | AO3 | 530 | V5_N2_CONT | N2 Gas Valve Control
|  | 17 | 5 | 4 | AO4 | 531
750-559 | 4-Chan Analog Out 0-10Vdc | 20 | 6 | 1 | AO1 | 532 | V6_CO2_CONT | CO2 Gas Valve Control
|  | 20 | 6 | 2 | AO2 | 533 | V6_O2_CONT | O2 Gas Valve Control
|  | 20 | 6 | 3 | AO3 | 534 | V6_N2_CONT | N2 Gas Valve Control
|  | 20 | 6 | 4 | AO4 | 535
750-559 | 4-Chan Analog Out 0-10Vdc | 23 | 7 | 1 | AO1 | 536 | V7_CO2_CONT | CO2 Gas Valve Control
|  | 23 | 7 | 2 | AO2 | 537 | V7_O2_CONT | O2 Gas Valve Control
|  | 23 | 7 | 3 | AO3 | 538 | V7_N2_CONT | N2 Gas Valve Control
|  | 23 | 7 | 4 | AO4 | 539
750-559 | 4-Chan Analog Out 0-10Vdc | 26 | 8 | 1 | AO1 | 540 | V8_CO2_CONT | CO2 Gas Valve Control
|  | 26 | 8 | 2 | AO2 | 541 | V8_O2_CONT | O2 Gas Valve Control
|  | 26 | 8 | 3 | AO3 | 542 | V8_N2_CONT | N2 Gas Valve Control
|  | 26 | 8 | 4 | AO4 | 543
750-559 | 4-Chan Analog Out 0-10Vdc | 29 | 9 | 1 | AO1 | 544 | V9_CO2_CONT | CO2 Gas Valve Control
|  | 29 | 9 | 2 | AO2 | 545 | V9_O2_CONT | O2 Gas Valve Control
|  | 29 | 9 | 3 | AO3 | 546 | V9_N2_CONT | N2 Gas Valve Control
|  | 29 | 9 | 4 | AO4 | 547
750-559 | 4-Chan Analog Out 0-10Vdc | 33 | 10 | 1 | AO1 | 548 | V10_CO2_CONT | CO2 Gas Valve Control
|  | 33 | 10 | 2 | AO2 | 549 | V10_O2_CONT | O2 Gas Valve Control
|  | 33 | 10 | 3 | AO3 | 550 | V10_N2_CONT | N2 Gas Valve Control
|  | 33 | 10 | 4 | AO4 | 551
750-559 | 4-Chan Analog Out 0-10Vdc | 36 | 11 | 1 | AO1 | 552 | V11_CO2_CONT | CO2 Gas Valve Control
|  | 36 | 11 | 2 | AO2 | 553 | V11_O2_CONT | O2 Gas Valve Control
|  | 36 | 11 | 3 | AO3 | 554 | V11_N2_CONT | N2 Gas Valve Control
|  | 36 | 11 | 4 | AO4 | 555
750-559 | 4-Chan Analog Out 0-10Vdc | 39 | 12 | 1 | AO1 | 556 | V12_CO2_CONT | CO2 Gas Valve Control
|  | 39 | 12 | 2 | AO2 | 557 | V12_O2_CONT | O2 Gas Valve Control
|  | 39 | 12 | 3 | AO3 | 558 | V12_N2_CONT | N2 Gas Valve Control
|  | 39 | 12 | 4 | AO4 | 559
750-559 | 4-Chan Analog Out 0-10Vdc | 42 | 13 | 1 | AO1 | 560 | V13_CO2_CONT | CO2 Gas Valve Control
|  | 42 | 13 | 2 | AO2 | 561 | V13_O2_CONT | O2 Gas Valve Control
|  | 42 | 13 | 3 | AO3 | 562 | V13_N2_CONT | N2 Gas Valve Control
|  | 42 | 13 | 4 | AO4 | 563
750-559 | 4-Chan Analog Out 0-10Vdc | 45 | 14 | 1 | AO1 | 564 | V14_CO2_CONT | CO2 Gas Valve Control
|  | 45 | 14 | 2 | AO2 | 565 | V14_O2_CONT | O2 Gas Valve Control
|  | 45 | 14 | 3 | AO3 | 566 | V14_N2_CONT | N2 Gas Valve Control
|  | 45 | 14 | 4 | AO4 | 567
750-559 | 4-Chan Analog Out 0-10Vdc | 48 | 15 | 1 | AO1 | 568 | V15_CO2_CONT | CO2 Gas Valve Control
|  | 48 | 15 | 2 | AO2 | 569 | V15_O2_CONT | O2 Gas Valve Control
|  | 48 | 15 | 3 | AO3 | 570 | V15_N2_CONT | N2 Gas Valve Control
|  | 48 | 15 | 4 | AO4 | 571
750-559 | 4-Chan Analog Out 0-10Vdc | 51 | 16 | 1 | AO1 | 572 | V16_CO2_CONT | CO2 Gas Valve Control
|  | 51 | 16 | 2 | AO2 | 573 | V16_O2_CONT | O2 Gas Valve Control
|  | 51 | 16 | 3 | AO3 | 574 | V16_N2_CONT | N2 Gas Valve Control
|  | 51 | 16 | 4 | AO4 | 575
750-1504 | 16-Chan Digital Out 24Vdc | 6 | 1 | 1 | DO1 | 576 | C1_H_SIG | Conditioning Tank Heater
|  | 6 | 1 | 2 | DO2 |  | E1_H_SIG | Experimental Tank Heater
|  | 6 | 2 | 3 | DO3 |  | C2_H_SIG | Conditional Tank Heater
|  | 6 | 2 | 4 | DO4 |  | E2_H_SIG | Experimental Tank Heater
|  | 6 | 3 | 5 | DO5 |  | C3_H_SIG | Conditional Tank Heater
|  | 6 | 3 | 6 | DO6 |  | E3_H_SIG | Experimental Tank Heater
|  | 6 | 4 | 7 | DO7 |  | C4_H_SIG | Conditional Tank Heater
|  | 6 | 4 | 8 | DO8 |  | E4_H_SIG | Experimental Tank Heater
|  | 6 | 5 | 9 | DO9 |  | C5_H_SIG | Conditional Tank Heater
|  | 6 | 5 | 10 | D10 |  | E5_H_SIG | Experimental Tank Heater
|  | 6 | 6 | 11 | D11 |  | C6_H_SIG | Conditional Tank Heater
|  | 6 | 6 | 12 | D12 |  | E6_H_SIG | Experimental Tank Heater
|  | 6 | 7 | 13 | D13 |  | C7_H_SIG | Conditional Tank Heater
|  | 6 | 7 | 14 | D14 |  | E7_H_SIG | Experimental Tank Heater
|  | 6 | 8 | 15 | D15 |  | C8_H_SIG | Conditional Tank Heater
|  | 6 | 8 | 16 | D16 |  | E8_H_SIG | Experimental Tank Heater
750-1504 | 16-Chan Digital Out 24Vdc | 32 | 9 | 1 | DO1 | 577 | C9_H_SIG | Conditioning Tank Heater
|  | 32 | 9 | 2 | DO2 |  | E9_H_SIG | Experimental Tank Heater
|  | 32 | 10 | 3 | DO3 |  | C10_H_SIG | Conditional Tank Heater
|  | 32 | 10 | 4 | DO4 |  | E10_H_SIG | Experimental Tank Heater
|  | 32 | 11 | 5 | DO5 |  | C11_H_SIG | Conditional Tank Heater
|  | 32 | 11 | 6 | DO6 |  | E11_H_SIG | Experimental Tank Heater
|  | 32 | 12 | 7 | DO7 |  | C12_H_SIG | Conditional Tank Heater
|  | 32 | 12 | 8 | DO8 |  | E12_H_SIG | Experimental Tank Heater
|  | 32 | 13 | 9 | DO9 |  | C13_H_SIG | Conditional Tank Heater
|  | 32 | 13 | 10 | D10 |  | E13_H_SIG | Experimental Tank Heater
|  | 32 | 14 | 11 | D11 |  | C14_H_SIG | Conditional Tank Heater
|  | 32 | 14 | 12 | D12 |  | E14_H_SIG | Experimental Tank Heater
|  | 32 | 15 | 13 | D13 |  | C15_H_SIG | Conditional Tank Heater
|  | 32 | 15 | 14 | D14 |  | E15_H_SIG | Experimental Tank Heater
|  | 32 | 16 | 15 | D15 |  | C16_H_SIG | Conditional Tank Heater
|  | 32 | 16 | 16 | D16 |  | E16_H_SIG | Experimental Tank Heater

## SW Assignments - Printable
Wago | Description | Mod | Tank | Chan | Wago Signal | Register | Signal Name | Signal Description
750-352 | Ethernet TCP/IP Fieldbus coupler
750-468 | 4-Chan Analog In 0-10Vdc | 3 | 1 | 1 | AI1 | 0 | C1_PH_SIG | Conditioning Tank pH
|  | 3 | 1 | 2 | AI2 | 1 | C1_O2_SIG | Conditioning Tank O2
|  | 3 | 1 | 3 | AI3 | 2 | E1_PH_SIG | Experimental Tank pH
|  | 3 | 1 | 4 | AI4 | 3 | E1_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 9 | 2 | 1 | AI1 | 4 | C2_PH_SIG | Conditioning Tank pH
|  | 9 | 2 | 2 | AI2 | 5 | C2_O2_SIG | Conditioning Tank O2
|  | 9 | 2 | 3 | AI3 | 6 | E2_PH_SIG | Experimental Tank pH
|  | 9 | 2 | 4 | AI4 | 7 | E2_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 12 | 3 | 1 | AI1 | 8 | C3_PH_SIG | Conditioning Tank pH
|  | 12 | 3 | 2 | AI2 | 9 | C3_O2_SIG | Conditioning Tank O2
|  | 12 | 3 | 3 | AI3 | 10 | E3_PH_SIG | Experimental Tank pH
|  | 12 | 3 | 4 | AI4 | 11 | E3_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 15 | 4 | 1 | AI1 | 12 | C4_PH_SIG | Conditioning Tank pH
|  | 15 | 4 | 2 | AI2 | 13 | C4_O2_SIG | Conditioning Tank O2
|  | 15 | 4 | 3 | AI3 | 14 | E4_PH_SIG | Experimental Tank pH
|  | 15 | 4 | 4 | AI4 | 15 | E4_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 18 | 5 | 1 | AI1 | 16 | C5_PH_SIG | Conditioning Tank pH
|  | 18 | 5 | 2 | AI2 | 17 | C5_O2_SIG | Conditioning Tank O2
|  | 18 | 5 | 3 | AI3 | 18 | E5_PH_SIG | Experimental Tank pH
|  | 18 | 5 | 4 | AI4 | 19 | E5_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 21 | 6 | 1 | AI1 | 20 | C6_PH_SIG | Conditioning Tank pH
|  | 21 | 6 | 2 | AI2 | 21 | C6_O2_SIG | Conditioning Tank O2
|  | 21 | 6 | 3 | AI3 | 22 | E6_PH_SIG | Experimental Tank pH
|  | 21 | 6 | 4 | AI4 | 23 | E6_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 24 | 7 | 1 | AI1 | 24 | C7_PH_SIG | Conditioning Tank pH
|  | 24 | 7 | 2 | AI2 | 25 | C7_O2_SIG | Conditioning Tank O2
|  | 24 | 7 | 3 | AI3 | 26 | E7_PH_SIG | Experimental Tank pH
|  | 24 | 7 | 4 | AI4 | 27 | E7_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 27 | 8 | 1 | AI1 | 28 | C8_PH_SIG | Conditioning Tank pH
|  | 27 | 8 | 2 | AI2 | 29 | C8_O2_SIG | Conditioning Tank O2
|  | 27 | 8 | 3 | AI3 | 30 | E8_PH_SIG | Experimental Tank pH
|  | 27 | 8 | 4 | AI4 | 31 | E8_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 30 | 9 | 1 | AI1 | 32 | C9_PH_SIG | Conditioning Tank pH
|  | 30 | 9 | 2 | AI2 | 33 | C9_O2_SIG | Conditioning Tank O2
|  | 30 | 9 | 3 | AI3 | 34 | E9_PH_SIG | Experimental Tank pH
|  | 30 | 9 | 4 | AI4 | 35 | E9_02_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 34 | 10 | 1 | AI1 | 36 | C10_PH_SIG | Conditioning Tank pH
|  | 34 | 10 | 2 | AI2 | 37 | C10_O2_SIG | Conditioning Tank O2
|  | 34 | 10 | 3 | AI3 | 38 | E10_PH_SIG | Experimental Tank pH
|  | 34 | 10 | 4 | AI4 | 39 | E10_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 37 | 11 | 1 | AI1 | 40 | C11_PH_SIG | Conditioning Tank pH
|  | 37 | 11 | 2 | AI2 | 41 | C11_O2_SIG | Conditioning Tank O2
|  | 37 | 11 | 3 | AI3 | 42 | E11_PH_SIG | Experimental Tank pH
|  | 37 | 11 | 4 | AI4 | 43 | E11_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 40 | 12 | 1 | AI1 | 44 | C12_PH_SIG | Conditioning Tank pH
|  | 40 | 12 | 2 | AI2 | 45 | C12_O2_SIG | Conditioning Tank O2
|  | 40 | 12 | 3 | AI3 | 46 | E12_PH_SIG | Experimental Tank pH
|  | 40 | 12 | 4 | AI4 | 47 | E12_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 43 | 13 | 1 | AI1 | 48 | C13_PH_SIG | Conditioning Tank pH
|  | 43 | 13 | 2 | AI2 | 49 | C13_O2_SIG | Conditioning Tank O2
|  | 43 | 13 | 3 | AI3 | 50 | E13_PH_SIG | Experimental Tank pH
|  | 43 | 13 | 4 | AI4 | 51 | E13_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 46 | 14 | 1 | AI1 | 52 | C14_PH_SIG | Conditioning Tank pH
|  | 46 | 14 | 2 | AI2 | 53 | C14_O2_SIG | Conditioning Tank O2
|  | 46 | 14 | 3 | AI3 | 54 | E14_PH_SIG | Experimental Tank pH
|  | 46 | 14 | 4 | AI4 | 55 | E14_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 49 | 15 | 1 | AI1 | 56 | C15_PH_SIG | Conditioning Tank pH
|  | 49 | 15 | 2 | AI2 | 57 | C15_O2_SIG | Conditioning Tank O2
|  | 49 | 15 | 3 | AI3 | 58 | E15_PH_SIG | Experimental Tank pH
|  | 49 | 15 | 4 | AI4 | 59 | E15_O2_SIG | Experimental Tank O2
750-468 | 4-Chan Analog In 0-10Vdc | 52 | 16 | 1 | AI1 | 60 | C16_PH_SIG | Conditioning Tank pH
|  | 52 | 16 | 2 | AI2 | 61 | C16_O2_SIG | Conditioning Tank O2
|  | 52 | 16 | 3 | AI3 | 62 | E16_PH_SIG | Experimental Tank pH
|  | 52 | 16 | 4 | AI4 | 63 | E16_O2_SIG | Experimental Tank O2
750-460 | 4-Chan Analog In RTD | 4 | 1 | 1 | R1+/R1- | 64 | C1_T_SIG | Conditioning Tank Temperature
|  | 4 | 1 | 2 | R2+/R2- | 65 | E1_T_SIG | Experimental Tank Temperature
|  | 4 | 1 | 3 | R3+/R3- | 66 | B1_T_SIG | Water Bath Temperature
|  | 4 | 1 | 4 | R4+/R4- | 67
750-460 | 4-Chan Analog In RTD | 10 | 2 | 1 | R1+/R1- | 68 | C2_T_SIG | Conditioning Tank Temperature
|  | 10 | 2 | 2 | R2+/R2- | 69 | E2_T_SIG | Experimental Tank Temperature
|  | 10 | 2 | 3 | R3+/R3- | 70 | B2_T_SIG | Water Bath Temperature
|  | 10 | 2 | 4 | R4+/R4- | 71
750-460 | 4-Chan Analog In RTD | 13 | 3 | 1 | R1+/R1- | 72 | C3_T_SIG | Conditioning Tank Temperature
|  | 13 | 3 | 2 | R2+/R2- | 73 | E3_T_SIG | Experimental Tank Temperature
|  | 13 | 3 | 3 | R3+/R3- | 74 | B3_T_SIG | Water Bath Temperature
|  | 13 | 3 | 4 | R4+/R4- | 75
750-460 | 4-Chan Analog In RTD | 16 | 4 | 1 | R1+/R1- | 76 | C4_T_SIG | Conditioning Tank Temperature
|  | 16 | 4 | 2 | R2+/R2- | 77 | E4_T_SIG | Experimental Tank Temperature
|  | 16 | 4 | 3 | R3+/R3- | 78 | B4_T_SIG | Water Bath Temperature
|  | 16 | 4 | 4 | R4+/R4- | 79
750-460 | 4-Chan Analog In RTD | 19 | 5 | 1 | R1+/R1- | 80 | C5_T_SIG | Conditioning Tank Temperature
|  | 19 | 5 | 2 | R2+/R2- | 81 | E5_T_SIG | Experimental Tank Temperature
|  | 19 | 5 | 3 | R3+/R3- | 82 | B5_T_SIG | Water Bath Temperature
|  | 19 | 5 | 4 | R4+/R4- | 83
750-460 | 4-Chan Analog In RTD | 22 | 6 | 1 | R1+/R1- | 84 | C6_T_SIG | Conditioning Tank Temperature
|  | 22 | 6 | 2 | R2+/R2- | 85 | E6_T_SIG | Experimental Tank Temperature
|  | 22 | 6 | 3 | R3+/R3- | 86 | B6_T_SIG | Water Bath Temperature
|  | 22 | 6 | 4 | R4+/R4- | 87
750-460 | 4-Chan Analog In RTD | 25 | 7 | 1 | R1+/R1- | 88 | C7_T_SIG | Conditioning Tank Temperature
|  | 25 | 7 | 2 | R2+/R2- | 89 | E7_T_SIG | Experimental Tank Temperature
|  | 25 | 7 | 3 | R3+/R3- | 90 | B7_T_SIG | Water Bath Temperature
|  | 25 | 7 | 4 | R4+/R4- | 91
750-460 | 4-Chan Analog In RTD | 28 | 8 | 1 | R1+/R1- | 92 | C8_T_SIG | Conditioning Tank Temperature
|  | 28 | 8 | 2 | R2+/R2- | 93 | E8_T_SIG | Experimental Tank Temperature
|  | 28 | 8 | 3 | R3+/R3- | 94 | B8_T_SIG | Water Bath Temperature
|  | 28 | 8 | 4 | R4+/R4- | 95
750-460 | 4-Chan Analog In RTD | 31 | 9 | 1 | R1+/R1- | 96 | C9_T_SIG | Conditioning Tank Temperature
|  | 31 | 9 | 2 | R2+/R2- | 97 | E9_T_SIG | Experimental Tank Temperature
|  | 31 | 9 | 3 | R3+/R3- | 98 | B9_T_SIG | Water Bath Temperature
|  | 31 | 9 | 4 | R4+/R4- | 99
750-460 | 4-Chan Analog In RTD | 35 | 10 | 1 | R1+/R1- | 100 | C10_T_SIG | Conditioning Tank Temperature
|  | 35 | 10 | 2 | R2+/R2- | 101 | E10_T_SIG | Experimental Tank Temperature
|  | 35 | 10 | 3 | R3+/R3- | 102 | B10_T_SIG | Water Bath Temperature
|  | 35 | 10 | 4 | R4+/R4- | 103
750-460 | 4-Chan Analog In RTD | 38 | 11 | 1 | R1+/R1- | 104 | C11_T_SIG | Conditioning Tank Temperature
|  | 38 | 11 | 2 | R2+/R2- | 105 | E11_T_SIG | Experimental Tank Temperature
|  | 38 | 11 | 3 | R3+/R3- | 106 | B11_T_SIG | Water Bath Temperature
|  | 38 | 11 | 4 | R4+/R4- | 107
750-460 | 4-Chan Analog In RTD | 41 | 12 | 1 | R1+/R1- | 108 | C12_T_SIG | Conditioning Tank Temperature
|  | 41 | 12 | 2 | R2+/R2- | 109 | E12_T_SIG | Experimental Tank Temperature
|  | 41 | 12 | 3 | R3+/R3- | 110 | B12_T_SIG | Water Bath Temperature
|  | 41 | 12 | 4 | R4+/R4- | 111
750-460 | 4-Chan Analog In RTD | 44 | 13 | 1 | R1+/R1- | 112 | C13_T_SIG | Conditioning Tank Temperature
|  | 44 | 13 | 2 | R2+/R2- | 113 | E13_T_SIG | Experimental Tank Temperature
|  | 44 | 13 | 3 | R3+/R3- | 114 | B13_T_SIG | Water Bath Temperature
|  | 44 | 13 | 4 | R4+/R4- | 115
750-460 | 4-Chan Analog In RTD | 47 | 14 | 1 | R1+/R1- | 116 | C14_T_SIG | Conditioning Tank Temperature
|  | 47 | 14 | 2 | R2+/R2- | 117 | E14_T_SIG | Experimental Tank Temperature
|  | 47 | 14 | 3 | R3+/R3- | 118 | B14_T_SIG | Water Bath Temperature
|  | 47 | 14 | 4 | R4+/R4- | 119
750-460 | 4-Chan Analog In RTD | 50 | 15 | 1 | R1+/R1- | 120 | C15_T_SIG | Conditioning Tank Temperature
|  | 50 | 15 | 2 | R2+/R2- | 121 | E15_T_SIG | Experimental Tank Temperature
|  | 50 | 15 | 3 | R3+/R3- | 122 | B15_T_SIG | Water Bath Temperature
|  | 50 | 15 | 4 | R4+/R4- | 123
750-460 | 4-Chan Analog In RTD | 53 | 16 | 1 | R1+/R1- | 124 | C16_T_SIG | Conditioning Tank Temperature
|  | 53 | 16 | 2 | R2+/R2- | 125 | E16_T_SIG | Experimental Tank Temperature
|  | 53 | 16 | 3 | R3+/R3- | 126 | B16_T_SIG | Water Bath Temperature
|  | 53 | 16 | 4 | R4+/R4- | 127
750-559 | 4-Chan Analog Out 0-10Vdc | 2 | 1 | 1 | AO1 | 512 | V1_CO2_CONT | CO2 Gas Valve Control
|  | 2 | 1 | 2 | AO2 | 513 | V1_O2_CONT | O2 Gas Valve Control
|  | 2 | 1 | 3 | AO3 | 514 | V1_N2_CONT | N2 Gas Valve Control
|  | 2 | 1 | 4 | AO4 | 515
750-559 | 4-Chan Analog Out 0-10Vdc | 8 | 2 | 1 | AO1 | 516 | V2_CO2_CONT | CO2 Gas Valve Control
|  | 8 | 2 | 2 | AO2 | 517 | V2_O2_CONT | O2 Gas Valve Control
|  | 8 | 2 | 3 | AO3 | 518 | V2_N2_CONT | N2 Gas Valve Control
|  | 8 | 2 | 4 | AO4 | 519
750-559 | 4-Chan Analog Out 0-10Vdc | 11 | 3 | 1 | AO1 | 520 | V3_CO2_CONT | CO2 Gas Valve Control
|  | 11 | 3 | 2 | AO2 | 521 | V3_O2_CONT | O2 Gas Valve Control
|  | 11 | 3 | 3 | AO3 | 522 | V3_N2_CONT | N2 Gas Valve Control
|  | 11 | 3 | 4 | AO4 | 523
750-559 | 4-Chan Analog Out 0-10Vdc | 14 | 4 | 1 | AO1 | 524 | V4_CO2_CONT | CO2 Gas Valve Control
|  | 14 | 4 | 2 | AO2 | 525 | V4_O2_CONT | O2 Gas Valve Control
|  | 14 | 4 | 3 | AO3 | 526 | V4_N2_CONT | N2 Gas Valve Control
|  | 14 | 4 | 4 | AO4 | 527
750-559 | 4-Chan Analog Out 0-10Vdc | 17 | 5 | 1 | AO1 | 528 | V5_CO2_CONT | CO2 Gas Valve Control
|  | 17 | 5 | 2 | AO2 | 529 | V5_O2_CONT | O2 Gas Valve Control
|  | 17 | 5 | 3 | AO3 | 530 | V5_N2_CONT | N2 Gas Valve Control
|  | 17 | 5 | 4 | AO4 | 531
750-559 | 4-Chan Analog Out 0-10Vdc | 20 | 6 | 1 | AO1 | 532 | V6_CO2_CONT | CO2 Gas Valve Control
|  | 20 | 6 | 2 | AO2 | 533 | V6_O2_CONT | O2 Gas Valve Control
|  | 20 | 6 | 3 | AO3 | 534 | V6_N2_CONT | N2 Gas Valve Control
|  | 20 | 6 | 4 | AO4 | 535
750-559 | 4-Chan Analog Out 0-10Vdc | 23 | 7 | 1 | AO1 | 536 | V7_CO2_CONT | CO2 Gas Valve Control
|  | 23 | 7 | 2 | AO2 | 537 | V7_O2_CONT | O2 Gas Valve Control
|  | 23 | 7 | 3 | AO3 | 538 | V7_N2_CONT | N2 Gas Valve Control
|  | 23 | 7 | 4 | AO4 | 539
750-559 | 4-Chan Analog Out 0-10Vdc | 26 | 8 | 1 | AO1 | 540 | V8_CO2_CONT | CO2 Gas Valve Control
|  | 26 | 8 | 2 | AO2 | 541 | V8_O2_CONT | O2 Gas Valve Control
|  | 26 | 8 | 3 | AO3 | 542 | V8_N2_CONT | N2 Gas Valve Control
|  | 26 | 8 | 4 | AO4 | 543
750-559 | 4-Chan Analog Out 0-10Vdc | 29 | 9 | 1 | AO1 | 544 | V9_CO2_CONT | CO2 Gas Valve Control
|  | 29 | 9 | 2 | AO2 | 545 | V9_O2_CONT | O2 Gas Valve Control
|  | 29 | 9 | 3 | AO3 | 546 | V9_N2_CONT | N2 Gas Valve Control
|  | 29 | 9 | 4 | AO4 | 547
750-559 | 4-Chan Analog Out 0-10Vdc | 33 | 10 | 1 | AO1 | 548 | V10_CO2_CONT | CO2 Gas Valve Control
|  | 33 | 10 | 2 | AO2 | 549 | V10_O2_CONT | O2 Gas Valve Control
|  | 33 | 10 | 3 | AO3 | 550 | V10_N2_CONT | N2 Gas Valve Control
|  | 33 | 10 | 4 | AO4 | 551
750-559 | 4-Chan Analog Out 0-10Vdc | 36 | 11 | 1 | AO1 | 552 | V11_CO2_CONT | CO2 Gas Valve Control
|  | 36 | 11 | 2 | AO2 | 553 | V11_O2_CONT | O2 Gas Valve Control
|  | 36 | 11 | 3 | AO3 | 554 | V11_N2_CONT | N2 Gas Valve Control
|  | 36 | 11 | 4 | AO4 | 555
750-559 | 4-Chan Analog Out 0-10Vdc | 39 | 12 | 1 | AO1 | 556 | V12_CO2_CONT | CO2 Gas Valve Control
|  | 39 | 12 | 2 | AO2 | 557 | V12_O2_CONT | O2 Gas Valve Control
|  | 39 | 12 | 3 | AO3 | 558 | V12_N2_CONT | N2 Gas Valve Control
|  | 39 | 12 | 4 | AO4 | 559
750-559 | 4-Chan Analog Out 0-10Vdc | 42 | 13 | 1 | AO1 | 560 | V13_CO2_CONT | CO2 Gas Valve Control
|  | 42 | 13 | 2 | AO2 | 561 | V13_O2_CONT | O2 Gas Valve Control
|  | 42 | 13 | 3 | AO3 | 562 | V13_N2_CONT | N2 Gas Valve Control
|  | 42 | 13 | 4 | AO4 | 563
750-559 | 4-Chan Analog Out 0-10Vdc | 45 | 14 | 1 | AO1 | 564 | V14_CO2_CONT | CO2 Gas Valve Control
|  | 45 | 14 | 2 | AO2 | 565 | V14_O2_CONT | O2 Gas Valve Control
|  | 45 | 14 | 3 | AO3 | 566 | V14_N2_CONT | N2 Gas Valve Control
|  | 45 | 14 | 4 | AO4 | 567
750-559 | 4-Chan Analog Out 0-10Vdc | 48 | 15 | 1 | AO1 | 568 | V15_CO2_CONT | CO2 Gas Valve Control
|  | 48 | 15 | 2 | AO2 | 569 | V15_O2_CONT | O2 Gas Valve Control
|  | 48 | 15 | 3 | AO3 | 570 | V15_N2_CONT | N2 Gas Valve Control
|  | 48 | 15 | 4 | AO4 | 571
750-559 | 4-Chan Analog Out 0-10Vdc | 51 | 16 | 1 | AO1 | 572 | V16_CO2_CONT | CO2 Gas Valve Control
|  | 51 | 16 | 2 | AO2 | 573 | V16_O2_CONT | O2 Gas Valve Control
|  | 51 | 16 | 3 | AO3 | 574 | V16_N2_CONT | N2 Gas Valve Control
|  | 51 | 16 | 4 | AO4 | 575
750-1504 | 16-Chan Digital Out 24Vdc | 6 | 1 | 1 | DO1 | 576 | C1_H_SIG | Conditioning Tank Heater
|  | 6 | 1 | 2 | DO2 |  | E1_H_SIG | Experimental Tank Heater
|  | 6 | 2 | 3 | DO3 |  | C2_H_SIG | Conditional Tank Heater
|  | 6 | 2 | 4 | DO4 |  | E2_H_SIG | Experimental Tank Heater
|  | 6 | 3 | 5 | DO5 |  | C3_H_SIG | Conditional Tank Heater
|  | 6 | 3 | 6 | DO6 |  | E3_H_SIG | Experimental Tank Heater
|  | 6 | 4 | 7 | DO7 |  | C4_H_SIG | Conditional Tank Heater
|  | 6 | 4 | 8 | DO8 |  | E4_H_SIG | Experimental Tank Heater
|  | 6 | 5 | 9 | DO9 |  | C5_H_SIG | Conditional Tank Heater
|  | 6 | 5 | 10 | D10 |  | E5_H_SIG | Experimental Tank Heater
|  | 6 | 6 | 11 | D11 |  | C6_H_SIG | Conditional Tank Heater
|  | 6 | 6 | 12 | D12 |  | E6_H_SIG | Experimental Tank Heater
|  | 6 | 7 | 13 | D13 |  | C7_H_SIG | Conditional Tank Heater
|  | 6 | 7 | 14 | D14 |  | E7_H_SIG | Experimental Tank Heater
|  | 6 | 8 | 15 | D15 |  | C8_H_SIG | Conditional Tank Heater
|  | 6 | 8 | 16 | D16 |  | E8_H_SIG | Experimental Tank Heater
750-1504 | 16-Chan Digital Out 24Vdc | 32 | 9 | 1 | DO1 | 577 | C9_H_SIG | Conditioning Tank Heater
|  | 32 | 9 | 2 | DO2 |  | E9_H_SIG | Experimental Tank Heater
|  | 32 | 10 | 3 | DO3 |  | C10_H_SIG | Conditional Tank Heater
|  | 32 | 10 | 4 | DO4 |  | E10_H_SIG | Experimental Tank Heater
|  | 32 | 11 | 5 | DO5 |  | C11_H_SIG | Conditional Tank Heater
|  | 32 | 11 | 6 | DO6 |  | E11_H_SIG | Experimental Tank Heater
|  | 32 | 12 | 7 | DO7 |  | C12_H_SIG | Conditional Tank Heater
|  | 32 | 12 | 8 | DO8 |  | E12_H_SIG | Experimental Tank Heater
|  | 32 | 13 | 9 | DO9 |  | C13_H_SIG | Conditional Tank Heater
|  | 32 | 13 | 10 | D10 |  | E13_H_SIG | Experimental Tank Heater
|  | 32 | 14 | 11 | D11 |  | C14_H_SIG | Conditional Tank Heater
|  | 32 | 14 | 12 | D12 |  | E14_H_SIG | Experimental Tank Heater
|  | 32 | 15 | 13 | D13 |  | C15_H_SIG | Conditional Tank Heater
|  | 32 | 15 | 14 | D14 |  | E15_H_SIG | Experimental Tank Heater
|  | 32 | 16 | 15 | D15 |  | C16_H_SIG | Conditional Tank Heater
|  | 32 | 16 | 16 | D16 |  | E16_H_SIG | Experimental Tank Heater