## io-map
category | ID | A | B | C |  | coil | I/O | type | values | tag | timer |  |  | Variable | Memory | Type
valve | SV1 | fromEQ | SV3a | SV2b | [7 empty] | s_ | MODE | s_MODE |  | i
valve | SV2 | inAIR | SV1c | NAFLONa | [7 empty] | s0_ | OP | s_OP |  | i
valve | SV3 | SV1b | vent SV7b | fromDIC | [8 empty] | STEP | s_STEP |  | i
valve | SV4 | SODAb SV5b | SODAa SV7a | NAFLONb | [8 empty] | SV1 | s_SV1 | Y001 | b
valve | SV5 | SGASa | SODAb SV4a | LICORa | [8 empty] | SV2 | s_SV2 | Y002 | b
valve | SV6 | SV7c | SV8c | P1b | [8 empty] | SV3 | s_SV3 | Y003 | b
valve | SV7 | SV4b SODAa | vent SV3b | SV6a | [8 empty] | SV4 | s_SV4 | Y004 | b
valve | SV8 | toEQ | toDIC | SV6b | [8 empty] | SV5 | s_SV5 | Y005 | b
pump | P1 | LICORb | SV6a |  | licor pump | [7 empty] | SV6 | s_SV6 | Y006 | b
pump | P2 | seawater | P3a drain |  | seawater pump | [7 empty] | SV7 | s_SV7 | Y007 | b
pump | P3 | P2b drain | DIC |  | sample pump | [7 empty] | SV8 | s_SV8 | Y008 | b
pump | P4 | acid | DIC |  | acid pump | [7 empty] | P1 | s_P1 | Y101 | b
process | LICOR | SV5c | P1a |  | licor instrument | [7 empty] | P2 | s_P2 | Y102 | b
process | NAFLON | SV2c | SV4c | [9 empty] | P3 | s_P3 | Y103 | b
process | SODA | SV4b SV7a | SV4a SV5b | [9 empty] | P4 | s_P4 | Y104 | b
| SGAS | SV5a
relay
panel | [13 empty] | s0_MODE | DS1 | i
[14 empty] | s0_OP | DS2 | i
[14 empty] | s0_STEP | DS3 | i
[14 empty] | s0_SV1 | C1 | b
[14 empty] | s0_SV2 | C2 | b
[14 empty] | s0_SV3 | C3 | b
[14 empty] | s0_SV4 | C4 | b
[14 empty] | s0_SV5 | C5 | b
[14 empty] | s0_SV6 | C6 | b
[14 empty] | s0_SV7 | C7 | b
[14 empty] | s0_SV8 | C8 | b
[14 empty] | s0_P1 | C9 | b
[14 empty] | s0_P2 | C10 | b
[14 empty] | s0_P3 | C11 | b
[14 empty] | s0_P4 | C12 | b
[14 empty] | tp_ | C500:600
DS4000 | const | MODE_POR
DS4001 | const | MODE_OFF
DS4002 | const | MODE_MAN
DS4003 | const | MODE_AUTO

## state tables
| States | S0 | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10 | S11 | S12 | S13 | S14
Actuator | Values | Rest | Meas/Eq | Air | Std Gas | Zero | Purge Eq | Fill Eq | Purge Sea | Fill DIC | Purge DIC/Air | Zero DIC/Air | Acidify | Meas DIC | DIC Drain | Manual
SV1 | A/B/X | bar: S14
SV2 | A/B/X | bar: S14
SV3 | A/B/X | bar: S14
SV4 | A/B/X | bar: S14
SV5 | A/B/X | bar: S14
SV6 | A/B/X | bar: S14
SV7 | A/B/X | bar: S14
SV8 | A/B/X | bar: S14
P1 | On/Off | bar: S14
P2 | On/Off | bar: S14
P3 | On/Off | bar: S14
P4 | On/Off | bar: S14
The system state vector consists of the value state of each system actuator, registers and UI inputs
sequences are defined by a set of unique system state vectors with transitions triggered by a period or event
transitions define sub-states (state vectors) with order and timing for state vector elements that change
The system has 3 modes: Hand, Off, Auto
In each mode, a set of UI inputs are enabled/disabled
Sequence | State | S0: x event; S1: x action(s)
zero cal | Air | S2: intake air
close air valve
| Zero | S0: 30s; S2: strip air of CO2 (via soda lime)
zero detector
high cal |  | S1: open span gas intake
| Std Gas | S2: flush span path w/ std gas
| Meas | S0: 10s; S2: licor measurement 10s @ 2Hz
acidify | Acidify | S1: close/open ? valves
acid pump ON
| Fill DIC | S0: time/vol; S2: flush and fill measured acid volume
|  | vol | acid pump OFF
Fill EQ
measure | Air | S0: 30s; S2: bubble air thru acid in zero loop to remove CO2
|  | 30s |  | flush sample volume
fill 1 ml sample volume
inject sample volume into EQ chamber
|  | 5m |  | bubble air thru acidified seawater EQ loop
turn off air circ pump
measure xCO2 w/ Licor
purge |  | S2: purge acidified sample
strip air of CO2 (via soda lime)
rest

## network
PLC | mac | IP
cw-plc |  | 192.168.0.10

## addr-map
Address | Data Type | Nickname | Initial Value | Retentive | Address Comment
SC1 | BIT | _Always_ON | 0 | No
SC2 | BIT | _1st_SCAN | 0 | No
SC3 | BIT | _SCAN_Clock | 0 | No
SC4 | BIT | _10ms_Clock | 0 | No
SC5 | BIT | _100ms_Clock | 0 | No
SC6 | BIT | _500ms_Clock | 0 | No
SC7 | BIT | _1sec_Clock | 0 | No
SC8 | BIT | _1min_Clock | 0 | No
SC9 | BIT | _1hour_Clock | 0 | No
SC10 | BIT | _Mode_Switch | 0 | No
SC11 | BIT | _PLC_Mode | 0 | No
SC19 | BIT | _PLC Error | 0 | No
SC20 | BIT | _I/O Module Error | 0 | No
SC21 | BIT | _System Config Error | 0 | No
SC22 | BIT | _I/O Config Error | 0 | No
SC23 | BIT | _Memory Check Error | 0 | No
SC24 | BIT | _Project File Error | 0 | No
SC25 | BIT | _Firmware Version Error | 0 | No
SC26 | BIT | _Watchdog Timer Error | 0 | No
SC27 | BIT | _Lost SDRAM Data | 0 | No
SC28 | BIT | _Battery Low Voltage | 0 | No
SC29 | BIT | _Battery Replacement | 0 | No
SC30 | BIT | _Run Edit Project Error | 0 | No
SC40 | BIT | _Division_Error | 0 | No
SC43 | BIT | _Out_of_Range | 0 | No
SC44 | BIT | _Address_Error | 0 | No
SC46 | BIT | _Math_Operation_Error | 0 | No
SC50 | BIT | _PLC_Mode_Change_to_STOP | 0 | No
SC51 | BIT | _Watchdog_Timer_Reset | 0 | No
SC53 | BIT | _RTC_Date_Change | 0 | No
SC54 | BIT | _RTC_Date_Change_Error | 0 | No
SC55 | BIT | _RTC_Time_Change | 0 | No
SC56 | BIT | _RTC_Time_Change_Error | 0 | No
SC90 | BIT | _Port_1_Ready_Flag | 0 | No
SC91 | BIT | _Port_1_Error_Flag | 0 | No
SC92 | BIT | _Port_1_Connection_Limit | 0 | No
SC93 | BIT | _Port_1_IP_Resolved | 0 | No
SC94 | BIT | _Port_1_Link_Flag | 0 | No
SC95 | BIT | _Port_1_100MBIT_Flag | 0 | No
SC100 | BIT | _Port_2_Ready_Flag | 0 | No
SC101 | BIT | _Port_2_Error_Flag | 0 | No
SC102 | BIT | _Port_3_Ready_Flag | 0 | No
SC103 | BIT | _Port_3_Error_Flag | 0 | No
SC202 | BIT | _Fixed_Scan_Mode | 0 | No
SC203 | BIT | _Battery_Installed | 0 | No
SD1 | INT | _PLC_Error_Code | 0 | No
SD5 | INT | _Firmware_Version_L | 0 | No
SD6 | INT | _Firmware_Version_H | 0 | No
SD9 | INT | _Scan_Counter | 0 | No
SD10 | INT | _Current_Scan_Time | 0 | No
SD11 | INT | _Minimum_Scan_Time | 0 | No
SD12 | INT | _Maximum_Scan_Time | 0 | No
SD13 | INT | _Fixed_Scan_Time_Setup | 1 | No
SD19 | INT | _RTC_Year(4 digits) | 0 | No
SD20 | INT | _RTC_Year(2 digits) | 0 | No
SD21 | INT | _RTC_Month | 0 | No
SD22 | INT | _RTC_Day | 0 | No
SD23 | INT | _RTC_Day_of_The_Week | 0 | No
SD24 | INT | _RTC_Hour | 0 | No
SD25 | INT | _RTC_Minute | 0 | No
SD26 | INT | _RTC_Second | 0 | No
SD29 | INT | _RTC_New_Year(4 digits) | 0 | No
SD31 | INT | _RTC_New_Month | 0 | No
SD32 | INT | _RTC_New_Day | 0 | No
SD34 | INT | _RTC_New_Hour | 0 | No
SD35 | INT | _RTC_New_Minute | 0 | No
SD36 | INT | _RTC_New_Second | 0 | No
SD40 | INT | _Port1_Received_Data_Len | 0 | No
SD41 | INT | _Port1_No_Comm_Time | 0 | No
SD50 | INT | _Port2_Received_Data_Len | 0 | No
SD51 | INT | _Port2_No_Comm_Time | 0 | No
SD60 | INT | _Port3_Received_Data_Len | 0 | No
SD61 | INT | _Port3_No_Comm_Time | 0 | No
SD80 | INT | _IP_Address1 | 0 | No
SD81 | INT | _IP_Address2 | 0 | No
SD82 | INT | _IP_Address3 | 0 | No
SD83 | INT | _IP_Address4 | 0 | No
SD84 | INT | _Subnet_Mask1 | 0 | No
SD85 | INT | _Subnet_Mask2 | 0 | No
SD86 | INT | _Subnet_Mask3 | 0 | No
SD87 | INT | _Subnet_Mask4 | 0 | No
SD88 | INT | _Default_Gateway1 | 0 | No
SD89 | INT | _Default_Gateway2 | 0 | No
SD90 | INT | _Default_Gateway3 | 0 | No
SD91 | INT | _Default_Gateway4 | 0 | No
Y001 | BIT | SV1 | 0 | No | valve
Y002 | BIT | SV2 | 0 | No
Y003 | BIT | SV3 | 0 | No
Y004 | BIT | SV4 | 0 | No
Y005 | BIT | SV5 | 0 | No
Y006 | BIT | SV6 | 0 | No
Y007 | BIT | SV7 | 0 | No
Y008 | BIT | SV8 | 0 | No
Y009 | BIT | P1 | 0 | No
Y010 | BIT | P2 | 0 | No
Y011 | BIT | P3 | 0 | No
Y012 | BIT | P4 | 0 | No
C002 | BIT | op_pending | 0 | Yes | state
C100 | BIT | TP_IND_SV1 | 0 | Yes
C101 | BIT | TP_IND_SV2 | 0 | Yes
C102 | BIT | TP_IND_SV3 | 0 | Yes
C103 | BIT | TP_IND_SV4 | 0 | Yes
C104 | BIT | TP_IND_SV5 | 0 | Yes
C105 | BIT | TP_IND_SV6 | 0 | Yes
C106 | BIT | TP_IND_SV7 | 0 | Yes
C107 | BIT | TP_IND_SV8 | 0 | Yes
C108 | BIT | TP_IND_P1 | 0 | Yes
C109 | BIT | TP_IND_P2 | 0 | Yes
C110 | BIT | TP_IND_P3 | 0 | Yes
C111 | BIT | TP_IND_P4 | 0 | Yes
C112 | BIT | TP_B1 | 0 | Yes
C113 | BIT | TP_B2 | 0 | Yes
C114 | BIT | TP_B3 | 0 | Yes
C115 | BIT | TP_B4 | 0 | Yes
C116 | BIT | TP_B5 | 0 | Yes
C117 | BIT | TP_B6 | 0 | Yes
C118 | BIT | TP_B7 | 0 | Yes
C119 | BIT | TP_B8 | 0 | Yes
C120 | BIT | TP_B9 | 0 | Yes
C121 | BIT | TP_B10 | 0 | Yes
C122 | BIT | TP_B11 | 0 | Yes
C123 | BIT | TP_B12 | 0 | Yes
C124 | BIT | TP_B13 | 0 | Yes
C125 | BIT | TP_B14 | 0 | Yes
C126 | BIT | TP_B15 | 0 | Yes
C127 | BIT | TP_B16 | 0 | Yes
C128 | BIT | TP_B17 | 0 | Yes
C129 | BIT | TP_B18 | 0 | Yes
C130 | BIT | TP_B19 | 0 | Yes
C131 | BIT | TP_B20 | 0 | Yes
C132 | BIT | TP_B21 | 0 | Yes
C133 | BIT | TP_B22 | 0 | Yes
C134 | BIT | TP_B23 | 0 | Yes
C135 | BIT | TP_B24 | 0 | Yes
C136 | BIT | TP_B25 | 0 | Yes
C137 | BIT | TP_B26 | 0 | Yes
C138 | BIT | TP_B27 | 0 | Yes
C139 | BIT | TP_B28 | 0 | Yes
C140 | BIT | TP_B29 | 0 | Yes
C141 | BIT | TP_B30 | 0 | Yes
C142 | BIT | TP_B31 | 0 | Yes
C143 | BIT | TP_B32 | 0 | Yes
C144 | BIT | TP_B33 | 0 | Yes
C145 | BIT | TP_B34 | 0 | Yes
C146 | BIT | TP_B35 | 0 | Yes
C147 | BIT | TP_B36 | 0 | Yes
C148 | BIT | TP_B37 | 0 | Yes
C149 | BIT | TP_B38 | 0 | Yes
C150 | BIT | TP_B39 | 0 | Yes
C151 | BIT | TP_B40 | 0 | Yes
C152 | BIT | TP_B41 | 0 | Yes
C153 | BIT | TP_B42 | 0 | Yes
DS2000 | INT | req_mode | 0 | Yes | touch panel input
DS3000 | INT | mode_id | 0 | Yes | current mode
DS3001 | INT | op_id | 0 | Yes | current operation
DS3002 | INT | seq_id | 0 | Yes | current sequence
DS3003 | INT | step_id | 0 | Yes | current step
DS3004 | INT | x_stat | 0 | Yes | status_output
DS3005 | INT | MODE_POR | 0 | Yes | mode ID
DS3006 | INT | MODE_OFF | 0 | Yes | mode ID
DS3007 | INT | MODE_MAN | 0 | Yes | mode ID
DS3008 | INT | MODE_AUTO | 0 | Yes | mode ID
DS3009 | INT | MODE_ESTOP | 0 | Yes | mode ID
DS3010 | INT | MODE_RESET | 0 | Yes | mode ID
DS3011 | INT | OP_NOP | 0 | Yes | operation ID
DS3012 | INT | OP_ZERO_CAL | 0 | Yes | operation ID
DS3013 | INT | OP_SPAN_CAL | 0 | Yes | operation ID
DS3014 | INT | OP_MEASURE | 0 | Yes | operation ID
DS3015 | INT | OP_PURGE | 0 | Yes | operation ID
DS3016 | INT | SEQ_NOP | 0 | Yes | sequence ID
DS3017 | INT | SEQ_IN_ACID | 0 | Yes | sequence ID
DS3018 | INT | SEQ_IN_SGAS | 0 | Yes | sequence ID
DS3019 | INT | SEQ_IN_SAMPLE | 0 | Yes | sequence ID
DS3020 | INT | SEQ_IN_AIR | 0 | Yes | sequence ID
DS3021 | INT | SEQ_INJ_ACID | 0 | Yes | sequence ID
DS3022 | INT | SEQ_SET_ZPATH | 0 | Yes | sequence ID
DS3023 | INT | SEQ_SET_SPATH | 0 | Yes | sequence ID
DS3024 | INT | SEQ_SET_EPATH | 0 | Yes | sequence ID
DS3025 | INT | SEQ_SET_PPATH | 0 | Yes | sequence ID
DS3026 | INT | SEQ_CIRC | 0 | Yes | sequence ID
DS3027 | INT | SEQ_EVAC | 0 | Yes | sequence ID
DS3028 | INT | SEQ_SAMPLE_FLUSH | 0 | Yes | sequence ID
DS3029 | INT | SEQ_ZERO_DET | 0 | Yes | sequence ID
DS3030 | INT | SEQ_MEASURE | 0 | Yes | sequence ID
DS3031 | INT | STAT_ | 0 | Yes | status output
C001 | BIT | SV1_ESTOP | 0 | Yes
DH1 | HEX | tp_set_valves | 0 | Yes | touch panel valve bit field
DH2 | HEX | tp_set_pumps | 0 | Yes | touch panel valve bit field
DF1 | FLOAT | tp_p1_uliter | 0 | Yes | touch panel request
DS4000 | INT | tp_p1_msec | 0 | Yes | touch panel request
DS4001 | INT | tp_p1_strokes | 0 | Yes | touch panel request
DS4002 | INT | TP_MODE_SEL | 0 | Yes
DS4003 | INT | TP_INC_STROKES | 0 | Yes
DS4004 | INT | TP_DEC_STROKES | 0 | Yes
DS4005 | INT | TP_OP_PAUSE | 0 | Yes | touch panel request
DS4006 | INT | TP_OP_CANCEL | 0 | Yes | touch panel request
DS4007 | INT | TP_OP_RESET | 0 | Yes | touch panel request
DS4008 | INT | TP_OP_MZERO | 0 | Yes
DS4009 | INT | TP_OP_MSPAN | 0 | Yes
DS4010 | INT | TP_OP_MSAMPLE | 0 | Yes
DS4011 | INT | TP_SV1_OPEN | 0 | Yes
DS4012 | INT | TP_SV1_CLOSE | 0 | Yes
DS4013 | INT | TP_SV2_OPEN | 0 | Yes
DS4014 | INT | TP_SV2_CLOSE | 0 | Yes
DS4015 | INT | TP_SV3_OPEN | 0 | Yes
DS4016 | INT | TP_SV3_CLOSE | 0 | Yes
DS4017 | INT | TP_SV4_OPEN | 0 | Yes
DS4018 | INT | TP_SV4_CLOSE | 0 | Yes
DS4019 | INT | TP_SV5_OPEN | 0 | Yes
DS4020 | INT | TP_SV5_CLOSE | 0 | Yes
DS4021 | INT | TP_SV6_OPEN | 0 | Yes
DS4022 | INT | TP_SV6_CLOSE | 0 | Yes
DS4023 | INT | TP_SV7_OPEN | 0 | Yes
DS4024 | INT | TP_SV7_CLOSE | 0 | Yes
DS4025 | INT | TP_SV8_OPEN | 0 | Yes
DS4026 | INT | TP_SV8_CLOSE | 0 | Yes
DS4027 | INT | TP_P1_ON | 0 | Yes
DS4028 | INT | TP_P1_OFF | 0 | Yes
DS4029 | INT | TP_P2_ON | 0 | Yes
DS4030 | INT | TP_P2_OFF | 0 | Yes
DS4031 | INT | TP_P3_ON | 0 | Yes
DS4032 | INT | TP_P3_OFF | 0 | Yes
DS4033 | INT | TP_P4_ON | 0 | Yes
DS4034 | INT | TP_P4_OFF | 0 | Yes
DS4035 | INT | TP_I1 | 0 | Yes
DS4036 | INT | TP_I2 | 0 | Yes
DS4037 | INT | TP_I3 | 0 | Yes
DS4038 | INT | TP_I4 | 0 | Yes
DS4039 | INT | TP_I5 | 0 | Yes
DS4040 | INT | TP_I6 | 0 | Yes
DS4041 | INT | TP_I7 | 0 | Yes
DS4042 | INT | TP_I8 | 0 | Yes
DS4043 | INT | TP_I9 | 0 | Yes
DS4044 | INT | TP_I10 | 0 | Yes
DS4045 | INT | TP_I11 | 0 | Yes
DS4046 | INT | TP_I12 | 0 | Yes
DS4047 | INT | TP_I13 | 0 | Yes
DS4048 | INT | TP_I14 | 0 | Yes
DS4049 | INT | TP_I15 | 0 | Yes
DS4050 | INT | TP_I16 | 0 | Yes
DS4051 | INT | TP_I17 | 0 | Yes
DS4052 | INT | TP_I18 | 0 | Yes
DS4053 | INT | TP_I19 | 0 | Yes
DS4054 | INT | TP_I20 | 0 | Yes
DS4055 | INT | TP_I21 | 0 | Yes
DS4056 | INT | TP_I22 | 0 | Yes
DS4057 | INT | TP_I23 | 0 | Yes
DS4058 | INT | TP_I24 | 0 | Yes
DS4059 | INT | TP_I25 | 0 | Yes
DS4060 | INT | TP_I26 | 0 | Yes
DS4061 | INT | TP_I27 | 0 | Yes
DS4062 | INT | TP_I28 | 0 | Yes
DS4063 | INT | TP_I29 | 0 | Yes
DS4064 | INT | TP_I30 | 0 | Yes
DS4065 | INT | TP_I31 | 0 | Yes
DS4066 | INT | TP_I32 | 0 | Yes
DS4067 | INT | TP_I33 | 0 | Yes
DS4068 | INT | TP_I34 | 0 | Yes
DS4069 | INT | TP_I35 | 0 | Yes
DS4070 | INT | TP_I36 | 0 | Yes
DS4071 | INT | TP_I37 | 0 | Yes
DS4072 | INT | TP_I38 | 0 | Yes
DS4073 | INT | TP_I39 | 0 | Yes
DS4074 | INT | TP_I40 | 0 | Yes
DS4075 | INT | TP_I41 | 0 | Yes
DS4076 | INT | TP_I42 | 0 | Yes
DS4077 | INT | TP_I43 | 0 | Yes
DS4078 | INT | TP_I44 | 0 | Yes
DS4079 | INT | TP_I45 | 0 | Yes
DS4080 | INT | TP_I46 | 0 | Yes
DS4081 | INT | TP_I47 | 0 | Yes
DS4082 | INT | TP_I48 | 0 | Yes
DS4083 | INT | TP_I49 | 0 | Yes