## Sheet1
Wago | Description | Chan | Wago Signal | Reg | Coil | Signal Name | Signal Description | Sensor/Hardware | Sensor Part Number | Manuf | Sensor/Hardware | Sensor PN | Manuf
750-352 | Ethernet Fieldbus coupler
750-468 | 4-Chan AI 0-10Vdc | 1 | AI1 | 0 |  | C1PH | Conditioning Tank pH | Tris-Compatible Flat pH Sensor | FPH-BTA | Vernier
|  | 2 | AI2 | 1 |  | C1O2 | Conditioning Tank O2 | Optical Dissolved Oxygen Probe | ODO-BTA | Vernier
|  | 3 | AI3 | 2 |  | E1PH | Experimental Tank pH | Tris-Compatible Flat pH Sensor | FPH-BTA | Vernier
|  | 4 | AI4 | 3 |  | E1O2 | Experimental Tank O2 | Optical Dissolved Oxygen Probe | ODO-BTA | Vernier
750-460 | 4-Chan AI RTD | 1 | R1+/R1- | 4 |  | C1T | Conditioning Tank Temp | PT100 RTD Probe | PR-22-3-100-A-1/4-0900-M12 | Omega
|  | 2 | R2+/R2- | 5 |  | E1T | Experimental Tank Temp | PT100 RTD Probe | PR-22-3-100-A-1/4-0900-M12 | Omega
|  | 3 | R3+/R3- | 6 |  | B1T | Water Bath Temperature | PT100 RTD Probe | PR-22-3-100-A-1/4-0900-M12 | Omega
|  | 4 | R4+/R4- | 7 |  | [spare]
750-559 | 4-Chan AO 0-10Vdc | 1 | AO1 | 512 |  | CO2_CNTL | CO2 Gas Valve Control | EV-P Series Proportional Valve Driver Bd | EVPD-2 | Clippard | EVP Prop Solenoid Valve | EC-P-10-2550 | Clippard
|  | 2 | AO2 | 513 |  | O2_CNTL | O2 Gas Valve Control | EV-P Series Proportional Valve Driver Bd | EVPD-2 | Clippard | EVP Prop Solenoid Valve | EC-P-10-2550 | Clippard
|  | 3 | AO3 | 514 |  | N2_CNTL | N2 Gas Valve Control | EV-P Series Proportional Valve Driver Bd | EVPD-2 | Clippard | EVP Prop Solenoid Valve | EC-P-10-2550 | Clippard
|  | 4 | AO4 | 515 |  | [spare]
750-1504 | 16-Chan DO 24Vdc | 1 | DO1 | 516 | 1 | C1H | Conditioning Tank Heater | Solid State Relay 280VAC/8A out 15-32Vdc | DRA1-SPFE240D25 | Crydom | 750W Immersion Heater | HDL00041 | Tempco
|  | 2 | DO2 |  | 2 | E1H | Experimental Tank Heater | Solid State Relay 280VAC/8A out 15-32Vdc | DRA1-SPFE240D25 | Crydom | 750W Immersion Heater | HDL00041 | Tempco
|  | 3 | DO3 |  | 3
|  | 4 | DO4 |  | 4
|  | 5 | DO5 |  | 5
|  | 6 | DO6 |  | 6
|  | 7 | DO7 |  | 7
|  | 8 | DO8 |  | 8
|  | 9 | DO9 |  | 9
|  | 10 | DO10 |  | 10
|  | 11 | DO11 |  | 11
|  | 12 | DO12 |  | 12
|  | 13 | DO13 |  | 13
|  | 14 | DO14 |  | 14
|  | 15 | DO15 |  | 15
|  | 16 | DO16 |  | 16
750-610 | 24Vdc Power Supply
750-600 | Termination Module