## Sheet1
I/O Unit: | Aquaria_Rack_0 | Type: | SNAP-ENET-S64 | IP: | 192.168.0.1
MODULE | RACK | SLOT | CHANNEL | POINT | I/O | FUNCTION
SNAP-OAC5MA | 0 | 0 | 0 | 0 | SV-15 | Solenoid Valve 15 for N2 Supply
SNAP-OAC5MA | 0 | 0 | 1 | 1 | SV-16 | Solenoid Valve 16 for CO2 Supply
SNAP-OAC5MA | 0 | 0 | 2 | 2 | SV-17 | Solenoid Valve 17 for O2 Supply
SNAP-OAC5MA | 0 | 0 | 3 | 3 | SPARE | Unused
EMPTY | 0 | 1 |  | 4 |  | Unused
EMPTY | 0 | 1 |  | 5 |  | Unused
EMPTY | 0 | 1 |  | 6 |  | Unused
EMPTY | 0 | 1 |  | 7 |  | Unused
SNAP-ODC5R5 | 0 | 2 | 0 | 8 | SIERRA MFC-0 | MFC-0 Power Tank 3 N2
SNAP-ODC5R5 | 0 | 2 | 1 | 9 | SIERRA MFC-1 | MFC-0 Power Tank 3 CO2
SNAP-ODC5R5 | 0 | 2 | 2 | 10 | SIERRA MFC-2 | MFC-0 Power Tank 3 O2
SNAP-ODC5R5 | 0 | 2 | 3 | 11 | SIERRA MFC-3 | MFC-0 Power Tank 3 N2
SNAP-ODC5R5 | 0 | 3 | 0 | 12 | SIERRA MFC-4 | MFC-0 Power Tank 3 CO2
SNAP-ODC5R5 | 0 | 3 | 1 | 13 | SIERRA MFC-5 | MFC-0 Power Tank 3 O2
SNAP-ODC5R5 | 0 | 3 | 2 | 14 | SIERRA MFC-6 | MFC-0 Power Tank 3 N2
SNAP-ODC5R5 | 0 | 3 | 3 | 15 | SIERRA MFC-7 | MFC-0 Power Tank 3 CO2
SNAP-ODC5R5 | 0 | 4 | 0 | 16 | SIERRA MFC-8 | MFC-0 Power Tank 3 O2
SNAP-ODC5R5 | 0 | 4 | 1 | 17 | SIERRA MFC-9 | MFC-0 Power Tank 3 N2
SNAP-ODC5R5 | 0 | 4 | 2 | 18 | SPARE | Unused
SNAP-ODC5R5 | 0 | 4 | 3 | 19 | SPARE | Unused
EMPTY | 0 | 5 |  | 20 |  | Unused
EMPTY | 0 | 5 |  | 21 |  | Unused
EMPTY | 0 | 5 |  | 22 |  | Unused
EMPTY | 0 | 5 |  | 23 |  | Unused
SNAP-IDC5MA | 0 | 6 | 0 | 24 |  | Water Sensor-0 Tank 1 (defunct)
SNAP-IDC5MA | 0 | 6 | 1 | 25 |  | Water Sensor-1 Tank 2 (defunct)
SNAP-IDC5MA | 0 | 6 | 2 | 26 |  | Water Sensor-2 Tank 3 (defunct)
SNAP-IDC5MA | 0 | 6 | 3 | 27 | SPARE | Unused
SNAP-ODC5R5 | 0 | 7 | 0 | 28 | OPTODE-0 | Oxygen Sensor-0 Tank 1 Power
SNAP-ODC5R5 | 0 | 7 | 1 | 29 | OPTODE-1 | Oxygen Sensor-1 Tank 2 Power
SNAP-ODC5R5 | 0 | 7 | 2 | 30 | OPTODE-2 | Oxygen Sensor-2 Tank 3 Power
SNAP-ODC5R5 | 0 | 7 | 3 | 31 | OPTODE-3 | Oxygen Sensor-3 Tank 0 Power
SNAP-ODC5R5 | 0 | 8 | 0 | 32 | R-12 | Relay-12 Licor-2 Power Tank 3 (defunct)
SNAP-ODC5R5 | 0 | 8 | 1 | 33 | R-13 | Relay-13 Vacuum Pump-0 Power Tank 1 (defunct)
SNAP-ODC5R5 | 0 | 8 | 2 | 34 | R-14 | Relay-14 Vacuum Pump-0 Power Tank 2 (defunct)
SNAP-ODC5R5 | 0 | 8 | 3 | 35 | R-15 | Relay-15 Vacuum Pump-2 Power Tank 3 (defunct)
SNAP-ODC5R5 | 0 | 9 | 0 | 36 | SPARE | Unused
SNAP-ODC5R5 | 0 | 9 | 1 | 37 | SPARE | Unused
SNAP-ODC5R5 | 0 | 9 | 2 | 38 | SPARE | Unused
SNAP-ODC5R5 | 0 | 9 | 3 | 39 | LED_Light | Photo Light (defunct)
SNAP-ODC5R5 | 0 | 10 | 0 | 40 | SV-12 | Solenoid Valve 12 Tank 1 Makeup Water (defunct)
SNAP-ODC5R5 | 0 | 10 | 1 | 41 | SV-13 | Solenoid Valve 13 Tank 2 Makeup Water (defunct)
SNAP-ODC5R5 | 0 | 10 | 2 | 42 | SV-14 | Solenoid Valve 14 Tank 3 Makeup Water (defunct)
SNAP-ODC5R5 | 0 | 10 | 3 | 43 | SPARE | Unused
SNAP-ODC5R5 | 0 | 11 | 0 | 44 | R-0 | Relay-0 Vacuum Break Valves (R-13, 14, 15) (defunct)
SNAP-ODC5R5 | 0 | 11 | 1 | 45 | R-1 | Relay-1 Circulating Pump-0 Power Tank 1
SNAP-ODC5R5 | 0 | 11 | 2 | 46 | R-2 | Relay-2 Licor-0 Power Tank 1 (defunct)
SNAP-ODC5R5 | 0 | 11 | 3 | 47 | SPARE | Unused
SNAP-ODC5R5 | 0 | 12 | 0 | 48 | R-8 | Relay-8 Circulating Pump-1 Power Tank 2
SNAP-ODC5R5 | 0 | 12 | 1 | 49 | R-9 | Relay-9 Circulating Pump-2 Power Tank 3
SNAP-ODC5R5 | 0 | 12 | 2 | 50 | R-10 | Relay-10 Circulating Pump-3 Power Tank 0
SNAP-ODC5R5 | 0 | 12 | 3 | 51 | R-11 | Relay-11 Licor-1 Power Tank 2 (defunct)
SNAP-IDC5MA | 0 | 13 | 0 | 52 | R-3 | Relay-3 Emergency Stop (normally closed)
SNAP-IDC5MA | 0 | 13 | 1 | 53 | TANK-0-LEVEL | Tank-0 Level Switch (defunct)
SNAP-IDC5MA | 0 | 13 | 2 | 54 | O2-ALARM | O2 Alarm - High (from R4 Coil)
SNAP-IDC5MA | 0 | 13 | 3 | 55 | CO2-ALARM | CO2 Alarm - High (from R4 Coil)
SNAP-IDC5MA | 0 | 14 | 0 | 56 | O2-WARN | O2 Alarm - Warning
SNAP-IDC5MA | 0 | 14 | 1 | 57 | CO-WARN | CO2 Alarm - Warning
SNAP-IDC5MA | 0 | 14 | 2 | 58 | Water-Alarm | Sensing Loop Water Alarm (defunct)
SNAP-IDC5MA | 0 | 14 | 3 | 59 | SPARE | Unused
SNAP-IDC5MA | 0 | 15 | 0 | 60 | TANK-0-SW | Tank-0 Switch (on/off) Tank-1
SNAP-IDC5MA | 0 | 15 | 1 | 61 | TANK-1-SW | Tank-1 Switch (on/off) Tank-2
SNAP-IDC5MA | 0 | 15 | 2 | 62 | TANK-2-SW | Tank-2 Switch (on/off) Tank-3
SNAP-IDC5MA | 0 | 15 | 3 | 63 | TANK-3-SW | Tank-3 Switch (on/off) Reservior Tank-0
I/O Unit: | Aquaria_Rack_1 | Type: | SNAP-ENET-S64 | IP: | 192.168.0.2
SNAP-AOV-25 | 1 | 0 | 0 | 0 | MFC-0-S | MFC-0 Tank-3 N2 DC Command Signal
SNAP-AOV-25 | 1 | 0 | 1 | 1 | MFC-1-S | MFC-1 Tank-3 CO2 DC Command Signal
SNAP-AOV-25 | 1 | 1 | 0 | 4 | MFC-2-S | MFC-2 Tank-3 O2 DC Command Signal
SNAP-AOV-25 | 1 | 1 | 1 | 5 | MFC-3-S | MFC-3 Tank-2 N2 DC Command Signal
SNAP-AOV-25 | 1 | 2 | 0 | 8 | MFC-4-S | MFC-4 Tank-2 CO2 DC Command Signal
SNAP-AOV-25 | 1 | 2 | 1 | 9 | MFC-5-S | MFC-5 Tank-2 O2 DC Command Signal
SNAP-AOV-25 | 1 | 3 | 0 | 12 | MFC-6-S | MFC-6 Tank-1 N2 DC Command Signal
SNAP-AOV-25 | 1 | 3 | 1 | 13 | MFC-7-S | MFC-7 Tank-1 CO2 DC Command Signal
SNAP-AOV-25 | 1 | 4 | 0 | 16 | MFC-8-S | MFC-8 Tank-1 O2 DC Command Signal
SNAP-AOV-25 | 1 | 4 | 1 | 17 | MFC-9-S | MFC-9 Tank-0 N2 DC Command Signal
EMPTY | 1 | 5
EMPTY | 1 | 6
EMPTY | 1 | 7
SNAP-AIMA-iSRC | 1 | 8 | 0 | 32 | pH-T1 | Honeywell pH Probe Serial ID -900021
SNAP-AIMA-iSRC | 1 | 8 | 1 | 33 | pH-T2 | Honeywell pH Probe Serial ID -900001
SNAP-AIMA-iSRC | 1 | 9 | 0 | 36 | pH-T3 | Honeywell pH Probe Serial ID -900003
SNAP-AIMA-iSRC | 1 | 9 | 1 | 37 | pH-T0 | Honeywell pH Probe Serial ID -900002
SNAP-AIMV2-4 | 1 | 10 | 0 | 40
SNAP-AIMV2-4 | 1 | 10 | 1 | 41
SNAP-AIMV2-4 | 1 | 10 | 2 | 42
SNAP-AIMV2-4 | 1 | 10 | 3 | 43 | SUPPLY-VOLTS | 24VDC Supply Voltage Level
SNAP-AIV-4 | 1 | 11 | 0 | 44 | TANK-1-CO2 | Licor-0 Channel 1 Output Tank-1 (defunct)
SNAP-AIV-4 | 1 | 11 | 1 | 45 | TANK-2-CO2 | Licor-1 Channel 1 Output Tank-2 (defunct)
SNAP-AIV-4 | 1 | 11 | 2 | 46 | TANK-3-CO2 | Licor-2 Channel 1 Output Tank-3 (defunct)
SNAP-AIV-4 | 1 | 11 | 3 | 47 | SPARE
SNAP-AIR40K-4 | 1 | 12 | 0 | 48 | TANK-0-TEMP | Tank-0 Temperature (oF)
SNAP-AIR40K-4 | 1 | 12 | 1 | 49 | TANK-1-TEMP | Tank-1 Temperature (oF)
SNAP-AIR40K-4 | 1 | 12 | 2 | 50 | TANK-2-TEMP | Tank-2 Temperature (oF)
SNAP-AIR40K-4 | 1 | 12 | 3 | 51 | TANK-3-TEMP | Tank-3 Temperature (oF)
EMPTY | 1 | 13 |  |  |  | Unused
SNAP-pH/ORP | 1 | 14 | 0 | 56 | pH-PROBE-1 | pH Probe Input (defunct)
SNAP-pH/ORP | 1 | 14 | 1 | 57 | pH-PROBE-2 | pH Probe Input (defunct)
EMPTY | 1 | 15 |  |  |  | Unused