# MARS Low Voltage Power System

# Requirements

Prepared by University of Washington Applied Physics Laboratory

for the Monterey Bay Aquarium Research Institute

Version 0-09, Sep 28, 2023

Document Control Sheet

| Version | Date | Description | By |
| --- | --- | --- | --- |
| 0-00 | 06/14/2021 | Initial Draft | T. McGinnis |
| 0-01 | 06/23/2021 | Updates. Sent to MBARI for review and comments. | T. McGinnis |
| 0-02 | 12/02/2021 | Updates. Sent to MBARI for review and comments. | T. McGinnis |
| 0-03 | 01/12/2022 | Updates. | T. McGinnis |
| 0-04 | 03/08/2022 | Updates. | MBARI |
| 0-05 | 03/21/2022 | Update after 3/8/2022 telephone conference. Included discussed changes. Added User Interface and Data Archive sections | T. McGinnis |
| 0-06 | 07/28/2023 | Updates. Reviewed during weekly APL meeting. | T. McGinnis |
| 0-07 | 08/07/2023 | Fixed error in Requirement IP5. | T. McGinnis |
| 0-08 | 09/22/2023 | Incorporate updates received from MBARI on 9/22/23 | T. McGinnis. P. McGill |
| 0-09 | 09/28/2023 | Added barometric pressure measurement to Section 2.7 Engineering Sensors | T. McGinnis |

Signature Page

This document has been approved and released for use.

MBARI MARS System Engineer 	      _______________                      _	 __     __

Printed

Signed          				Date

UW/APL MARS System Engineer	      _______________                      _	 __     __

Printed

Signed          				Date

Table of Contents

1	General	5

1.1	Ocean Observatories Initiative (OOI) Overview	5

1.2	Document Scope and Purpose	5

1.3	Definitions	5

1.3.1	Acronyms	5

2	Requirements	6

2.1	Shore Medium Voltage Power Supply Control & Monitoring	6

2.2	Medium Voltage Converter Monitoring	6

2.3	Input Protection	7

2.4	Ground Fault Monitoring and Detection	7

2.5	Hotel Power	8

2.7	Engineering Sensors	10

2.8	User Interface	11

2.9	Data Archiving	11

# General

## Ocean Observatories Initiative (OOI) Overview

Most oceanographic instruments on the seafloor have no connections with the surface, so they run on batteries and store their own data. A cabled observatory like MARS removes those restrictions, allowing scientists to design new types of oceanographic equipment and study the ocean in new ways. MARS System shall provide electrical power and data connections for new research instruments in the deep-sea. That’s the vision behind the Monterey Accelerated Research System (MARS).

The system consists of a 52-km (32-mile) undersea cable that carries data and power to a “science node” 891 meters (2,923 feet) below the surface of Monterey Bay at North 36° 42.7481’ N, 122° 11.2139’ W. Up to eight different science instruments can be attached to the MARS using ROV-mateable connector ports. For each of the 8 ports, System shall provide switched 375VDC power, Gigabit Ethernet and precision timing. Additional experiments can be daisy-chained.

## Document Scope and Purpose

This document contains the requirements for the MARS Low Voltage Power System.

## Definitions

## Acronyms

- MBARI 		Monterey Bay Aquarium Research Institute

- MARS		Monterey Accelerated Research System

- UW 		University of Washington

- APL 		Applied Physics Laboratory

- NSF 		National Science Foundation

- OOI 		Oceans Observatories Initiative

- RCA		Regional Cabled Array

- RSN		Regional Scale Nodes

- ROV 		Remotely operated vehicle

- PBOF		Pressure balanced oil-filled

- LVPS		Low Voltage Power System

- PMACS		Power Monitoring and Control System

- MVPS		Medium Voltage Power Supply

- MVC		Medium Voltage Converter

- GFM		Ground Fault Monitoring

# Requirements

## Shore Medium Voltage Power Supply Control & Monitoring

| Req’t # | Requirement Description | Test Procedure Steps |
| --- | --- | --- |
| MP1 | Shore Medium Voltage Power Supply shall provide 1500VDC (nominal) | 2.6.2 – 2.6.5 |
| MP2 | The System shall provide the ability to remotely enable and disable the MVPS | 2.6.2 |
| MP3 | The System shall measure MVPS output voltage and current | 2.6.3 – 2.6.6 |
| MP4 | The System shall display MVPS output voltage and current measurements |  |
| MP5 | The System shall record MVPS output voltage and current measurements at a rate of at least 1Hz |  |

## Medium Voltage Converter Monitoring

| Req’t # | Requirement Description | Test Procedure Steps |
| --- | --- | --- |
| MC1 | J-Box Medium Voltage Converter shall provide two (2) isolated 375VDC (nominal) outputs for loads up to 4A/1500W each | 2.7.2 – 2.7.5 |
| MC2 | The two MVC outputs shall be isolated from each other |  |
| MC3 | System shall measure MVC input voltage and current for two 375VDC outputs |  |
| MC4 | System shall transmit the MVC voltage and current measurement data for two 375VDC outputs to the Node Controller in the LVPS housing |  |
| MC5 | System shall display MVC input voltage and current measurements for two 375VDC outputs |  |
| MC6 | System shall record MVC input voltage and current measurements for two 375VDC outputs at a rate of at least 1Hz |  |
| MC7 | System shall reference the two MVC 375VDC outputs to +/-187VDC, relative to sea water potential |  |

## Input Protection

| Req’t # | Requirement Description | Test Procedure Steps |
| --- | --- | --- |
| IP1 | LVPS shall have reverse voltage protection |  |
| IP2 | LVPS shall have over voltage protection (+10%) |  |

## Ground Fault Monitoring and Detection

| Req’t # | Requirement Description | Test Procedure Steps |
| --- | --- | --- |
| GF1 | System shall measure seawater Ground Fault Current on the +/-187VDC power circuits | 2.4.7, 2.4.8 |
| GF2 | System shall display seawater Ground Fault Current on the +/-187VDC power circuits |  |
| GF3 | System shall record seawater Ground Fault Current on the +/-187VDC power circuits |  |
| GF4 | System shall provide an alarm if the seawater Ground Fault Current exceeds a User Selectable level | 2.4.9 |

## Hotel Power

| Req’t # | Requirement Description | Test Procedure Steps |
| --- | --- | --- |
| HP1 | System shall provide unswitched 5VDC power to two (2) loads Qty; Current. 1; MBARI 1PPS Distribution; 0.1A. 1; Spare; 0.9A. | 2.3.3, 2.3.6, 2.3.7 |
| HP2 | System shall measure 5VDC Bus Current | 2.3.9, 2.3.10 |
| HP3 | System shall display 5VDC Bus Current |  |
| HP4 | System shall record 5VDC Bus Current at a rate of at least 1Hz |  |
| HP5 | System shall provide switched 24VDC power to four (4) loads Qty; Current. 2; Cisco IE3300 Router; 1.2A. 1; Meinberg SyncBox N2X; 0.44A. 1; Moxa IMC-101G Digi Portserver TS4 (combined); 0.16A 0.25A. | 2.3.4, 2.3.8 |
| HP6 | System shall measure 24VDC Current of the individual switched circuits |  |
| HP7 | System shall display 24VDC Bus Current of the individual switched circuits |  |
| HP8 | System shall record 24VDC Bus Current of the individual switched circuits at a rate of at least 1Hz |  |
| HP9 | System shall provide unswitched 24VDC power to three (3) loads Qty; Current. 1; MBARI MVC Monitor; ?. 2; Spare. | 2.3.5 |

| HP10 | System shall measure 24VDC Bus Current | 2.3.11, 2.3.12 |
| --- | --- | --- |
| HP11 | System shall display 24VDC Bus Current |  |
| HP12 | System shall record 24VDC Bus Current at a rate of at least 1Hz |  |
| HP13 | System shall provide 1 (one) unswitched, isolated 24VDC circuit to the MVC housing and monitoring electronics Qty; Current. 1; MBARI MVC Serial Monitor; ?. 2; Shaeffer K1846 MVC Logic Boards; ?. |  |
| HP14 | System shall measure the isolated 24VDC Bus Current |  |
| HP15 | System shall display the isolated 24VDC Bus Current |  |
| HP16 | System shall record the isolated 24VDC Bus Current at a rate of at least 1Hz |  |
| HP17 | Hotel Power Board input power shall be able to be supplied by either the Left or Right MVC |  |

  - Science Instrument Power

| Req’t # | Requirement Description | Test Procedure Steps |
| --- | --- | --- |
| IP1 | System shall provide switched 375VDC power supply to 8 external Science Instrument Ports | 2.5.3, 2.5.4 |
| IP2 | System shall provide full MVC current capacity of 375VDC of up to 4A to any individual Science Instrument Port (Note 1, below) | 2.5.5 – 2.5.13 |
| IP3 | System shall measure 375VDC load current monitoring to 8 Science Instrument Ports | 2.5.5 – 2.5.13 |
| IP4 | System shall provide the ability to fully galvanically isolate the 375VDC power supply circuitry from the Science Connectors | 2.5.14 – 2.5.22 |
| IP5 | System shall not allow the mechanical isolation relays to be closed after or opened before the solid-state switches (solid-state FETs will switch the load current) |  |
| IP6 | System shall provide User Adjustable Over-Current Protection to 8 Science Instrument Ports | 2.5.24 |
| IP7 | System shall provide In-Rush Current Time Trip to 8 Science Instrument Ports | 2.5.25 |

## Engineering Sensors

| Req’t # | Requirement Description | Test Procedure Steps |
| --- | --- | --- |
| ES1 | System shall provide temperature measurement, display and recording in the following locations: - Each printed circuit board (IGB, HPB, 2 x IPB) - FETs on IGB - 4 unassigned temp sensor inputs (IPB heatsinks?) |  |
| ES2 | System shall display temperature readings at the specified locations |  |
| ES3 | System shall record temperature reading at the specified locations at a rate of at least 1Hz |  |
| ES4 | System shall measure humidity in the pressure vessel | 2.4.5 |
| ES5 | System shall display humidity in the pressure vessel |  |
| ES6 | System shall provide an over-humidity alarm when the relative humidity exceeds TBD% |  |
| ES7 | System shall record humidity in the pressure vessel at a rate of at least 1Hz |  |
| ES8 | System shall measure barometric pressure in the pressure vessel |  |
| ES9 | System shall display barometric pressure in the pressure vessel |  |
| ES10 | System shall record barometric pressure in the pressure vessel at a rate of at least 1Hz |  |
| ES11 | System shall provide Over Temperature alarm and shutdown |  |

## User Interface

| Req’t # | Requirement Description | Test Procedure Step(s) |
| --- | --- | --- |
| UI1 | System shall provide a graphical user interface (GUI) that provides controls of the system functions and displays of the monitoring data |  |
| UI2 | The GUI shall allow switching the solid-state power switches for 8 external Science Instrument loads |  |
| UI3 | The GUI shall allow switching the solid-state power switches for 3 internal hotel loads |  |
| UI4 | The GUI shall allow switching the mechanical isolation relays for 8 external Science Instrument loads |  |
| UI5 | The GUI shall ask for confirmation of commands before actuating switches |  |
| UI6 | The GUI shall allow the user to enter the Adjustable Over-Current Trip levels |  |
| UI7 | The GUI shall display the external Science Port load currents |  |
|  | The GUI shall display the internal voltage bus currents |  |
| UI8 | The GUI shall issue & record alarms, TBD |  |
| UI9 | The GUI shall display temperature and humidity data |  |
| UI10 | The GUI shall display the ground fault current on the +/-187VDC busses |  |
| UI11 | The GUI shall display the input and output voltage and current of MVC-R & MVC-L |  |

## Data Archiving

| Req’t # | Requirement Description | Test Procedure Step(s) |
| --- | --- | --- |
| DA1 | System shall include a data archive on shore with all the monitor data |  |
| DA2 | The data archive shall record and store all data with a sample rate of 1 sample per second. |  |
| DA3 | The data archive shall provide a method to display and/or plot any user selected data over any time period from the archive |  |
| DA4 | The data archive shall include an event log with the times when commands are issued |  |

Notes:

- The Science Instrument Ports will be powered by 2 Instrument Power Boards (IPB). Each IPB will have 4 Science Instrument Ports that provide power from one of the two Medium Voltage Converters with a nominal capacity of 1500W/4A each. Each of the 2 IPBs will be able to supply up to the full MVC capacity to 1-4 connected Science Instrument Ports. One of the MVC converters will also provide power to the Hotel Loads so the IPB associated with that MVC will only be able to provide power up to 1500W/4A minus the total hotel load (approximately 100W).