Power for MARS Sub-node

Purpose:

To start discussion on what the characteristics of the cable for the proposed MARS sub-node extension need to be.

Assumptions:

- The 1860 meter site is the one being used so the cable length will be 8 kilometers.

- The cable will have two 16 AWG conductors.

- Vicors are used at tend of cable so min voltage is 250 vdc.

- For the purpose of this discussion, the MARS 375 volts is considered perfect.

Power to the MARS sub-node will be provided from the 375 volts.  Cable losses will still highly limit available power.  Resistance of 16 AWG wire is 13.12 ohms per kilometer.  The current estimate of an eight kilometer cable run means a total of 105 ohms in each conductor.  Power can be provided through the cable with two wires in two ways:

Utilizing one wire as power and the second wire as return

Utilizing both wires as power and seawater as return

Utilizing a two wire circuit doubles the total wire length and thus the resistance to 210 ohms.  Limiting voltage drop to 125 volts means a max current of approximately 0.6 amps or delivered power at the end of the cable of 150 watts.

Utilizing both wires as power cuts the total resistance to 52.5 ohms.  Limiting voltage drop to 125 volts means a max current of approximately 2.4 amps or delivered power at the end of the cable of 600 watts.