MONTEREY BAY AQUARIUM RESEARCH INSTITUTE

SAFE HANDLING PROCEDURES FOR FLUORINERT

FC-77 ELECTRONIC COOLANT IN MARS MV HOUSING

October 24, 2007

MARS Project

Safe Handling Procedures for Fluorinert FC-77

TABLE OF CONTENTS

I. Introduction

II. Properties and Hazards of Fluorinert FC-77

III. Manual Handling of FC-77

IV. Filling of MV Housing

V. Electronically Energizing the Power Supply Unit

VI. Draining FC-77 From the MV Housing

VII. Emergency Procedures

VIII. Waste Handling Procedures

IX. Appendices

MARS Project

Safe Handling Procedures for Fluorinert FC-77

I.

Introduction

Fluorinert FC-77 is a dielectric coolant fluid that is used in the MARS MV and LVhousings.  The approximate volume of FC-77 in the MV housing is 120 liters and X liters in the LV housing.  The purpose of these written procedures is to reduce the risk of injury associated with the handling and use of FC-77, including but not limited to the potential exposure to thermo-electrical decomposition products.

Because Fluorinert is also used in the LV housing, the same safety precautions must be taken with regards to handling of the Fluorinert, in particular the prevention of back injuries, potential shock/electrocution and spill prevention/response.  The lower voltage in the LV housing greatly reduces the risk of the formation of perfluoroisobutylene (PFIB), however, the same draining and purging safety procedures should be followed as for draining the MV housing since the procedures and equipment to do so are readily available.

It is the responsibility of supervisors to ensure that all their employees who work with Fluorinert FC-77 in the MARS applications are effectively informed and trained in the hazards and safe work practices referenced herein.  The safety training shall include:

Employees involved in the operation of the MARS power unit system shall have the following training prior to starting any work on the system.

- High Voltage Electrical Safety

  - Biological effects of electricity, shock: amperage v voltage; arc flash hazards

  - NFPA 70 work practices: approach boundaries, arc flash boundaries

  - Electrically safe condition: lock-out/tag out procedures

  - Signage, labeling

- Safe Lifting – Back Injury Prevention

  - Use of mechanical means to move/transfer FC-77

  - Proper lifting techniques

- First aid/cpr

  - Treatment for electrical shock/burn, electrocution

- Hazcom & Spill response for FC-77 releases

  - Physical properties and health effects, including potential  contaminants, i.e., hydrofluoric acid and PFIB

  - Labeling requirements:  Hazcom & Waste labeling

  - Safety, Isolate, Notify

  - Containment & absorption

  - PPE

  - Exhaust ventilation

- Emergency procedures – general

  - Electrical shock/electrocution

  - Fire

  - Spill response

- Hazardous materials/waste handling

  - Labeling requirements

  - Container selection – compatibility

  - Notification for waste pick-up/transfer

II. Properties and Hazards of FC-77

Appendices A and B provide information pertaining to the properties and hazards of Fluorinert FC-77.  Fluorinert is a hydrofluorocarbon liquid that is relatively non-toxic and non-combustible.  The hazards of fluorinert can be summarized as:

- high density, much greater than water; potential lifting/back injury hazard

- high density, potential environmental contamination

- toxic decomposition products upon exposure to temperatures in excess of 200 degrees Celsius

- volatile, dense vapors which can displace oxygen leading to asphyxiation.

Thermal decomposition of FC-77 leads to the formation of perfluorisobulylene, PFIB (see Appendices C and D).  PFIB is highly toxic by inhalation and hydrolyzes in water to form hydrofluoric acid.  Thermal decomposition starts above 200 degrees Celsius but does not progress substantially until in excess of 400 degrees.  PFIB is soluble in FC-77 and exists as a gas at room temperature and standard pressure.  It reacts rapidly with water, hydrolyzing eventually into hydrofluoric acid (HF).  There is the potential for PFIB to form in the MV housing should there be an electrical arc failure, e.g., arc short in MV converters.  The extent and duration of such an electrical arc failure can vary and may not be readily identifiable.  Thus, it must be assumed that PFIB could be present in the FC-77 from the MV housing should it become necessary to drain the unit.

There are a number of possible, though unlikely, electrical failure scenarios in the MARS MV or LV housings, could generate the 200-400 C temperatures needed to decompose FC-77.   Either an electrical arc or an overheated circuit element could supply the required power density... although vaporizing the liquid coolant and then maintaining the required temperatures for any length of time would require unusual circumstances.  As a general rule, though, the presence of toxic breakdown products should be suspected and guarded against anytime that FC-77 is removed from either the MV or LV Converters, and specifically under the following circumstances:

1) Any unexplained fault which causes either converter to stop operating.

2) Any event which causes either converter to draw higher than expected input power, given the output load; this particularly includes any event that current-limits an external power supply.

3) Any unexplained change in operating temperature or especially internal pressure inside either the MV or LV Housings.

4) Any time that either converter has operated unattended in the lab or un-monitored by telemetry during remote deployment.

In any of these scenarios (and possibly others), a high-energy electrical fault cannot be ruled out and therefore the presence of breakdown products, while unlikely, cannot safely be ruled out.

Based on the collective hazards of Fluorinert and its potential decomposition products, the following general practices must be followed:

- Use FC-77 in a well ventilated space

- Use mechanical means to void excessive lifting

- To the extent feasible, avoid exposure to high temperatures

- Keep spills out of storm drains and water ways.

In addition, the usage of dielectric coolants leads to concomitant hazards, i.e., exposure to electrically energized conductors and equipment with the potential for shock, electrocution and/or arc flash explosions.  All electrical work is to be done in accordance with NFPA 70E.

III. Manual Handling of FC-77

The following job hazard analyses are used to identify the steps, hazards and corresponding safe work practices when using and handling FC-77.  The sequence of tasks should be considered as step-by-step procedures.

| Task | Hazard | Safety Procedure |
| --- | --- | --- |
| Lifting, transport of containers | High density, muscle strain | Use mechanical means to lift and transport containers greater than 5 gal volume |
| Transfer of fluid | High density, muscle strain Potential splash and eye contact | Use mechanical means to pump or transfer large quantities of liquid. Position supply and receiving containers at the same level or have receiving container lower than supply container. Avoid any open transfer above shoulder height. Avoid any open transfer above shoulder height. Wear safety glasses with side shields during transfer operations. |

IV. Filling of MV and LV Housings

Because of the high specific gravity/density of FC-77, the lifting and movement of containers of the liquid present a significant risk of back injury or similar musculo-skeletal injury.  Emphasis must be placed on using mechanical means to lift and transfer the FC-77.

| Task | Hazard | Safety Procedure |
| --- | --- | --- |
| Physical contact with MV or LV housing, opening of fill port | Potential electrical shock | Lock-out/tag-out power supply – render power supply unit (PSU) into electrically safe condition, i.e., not energized. (ref. NFPA 70E) |
| Transfer of liquid Transfer of liquid | Potential muscle strain Potential spill of liquid: environmental contamination Accidental presence of air/moisture in MV or LV housings – potential to generate PFIB and HF should there also be an electrical arc event. | See I above Use mechanical pump means to transfer liquid; have spill response materials readily available. 2 employees minimum present Have means to prevent over filling of vessel. Evacuate vessel prior to filling; fill with closed system transfer; leave no headspace above FC-77 liquid |

V. Electrically Energizing Power Supply Unit

This procedure involves supplying electrical power to the unit and, thus, creating a serious potential for electrical shock, electrocution and/or arc flash explosion.  Particular care must therefore be paid to conducting said work according to the practices in NFPA 70E and only conducted by qualified individuals.

| Task | Hazard | Safety Procedure |
| --- | --- | --- |
| Physical connection of PSU to other system conductors | Potential electrical shock | Ensure no energized conductors during connection phase: Lock-out/tag-out power supply – render PSU vessel into electrically safe condition. (ref. NFPA 70E) 2 employees present minimum Establish approach boundaries and arc flash boundaries per NFPA 70E standard. Provide for required training and PPE per NFPA 70E for authorized operators. |
| Energizing Power Supply Unit | Potential electrical shock | Effectively communicate to those individuals within the restricted approach boundary of impending energizing of system. Use warning indicator lights or other equally effective means to indicate energized equipment. |
| Transient electrical failure, capacitor or insulation failure; arcing | Excess heating of dielectric fluid above 400 deg C, possible formation of polyfluoroisobutylene, PFIB, toxic inhalation hazard | Assume PFIB formed. Follow procedures for safe draining and collection of FC-77, and concomitant purging/trapping of possible PFIB. |

VI.  Draining FC-77 From the MV Housing

If power has been applied to the MV power converters, whether this has been performed in a lab on shore or during an ocean deployment, it should be assumed that HF or PFIB may be present in the MV housings, and the procedures below must be followed in order to drain the fluorinert from MV housing.

This procedure must be done using a closed system involving a recovery drum and purge & trap apparatus to capture and hydrolyze any PFIB that may be present (see Appendix E).  Either a fluoride ion probe can be included in the purge trap vessel or a sample of purge water can be drained from the purge/trap vessel and analysed with the floride ion probe.

General Precautions

a) Be attentive to leaks at pipe thread fittings, especially over time.  SAE and compression fittings preferred;

b) Avoid using materials that react with HF such as silica and glass;

c) Test for leaks at receiver drum and inlet to purge trap vessel prior to operation

.

| Task | Hazard | Safety Procedure |
| --- | --- | --- |
| De-energizing PSU | Potential electrical shock | Lock-out/tag-out power supply – render PSU into electrically safe condition. (ref. NFPA 70E) |
| Attach recovery drum and purge & trap apparatus (see Appendix E) | If PFIB is present, then potential inhalation - toxic exposure. If hydrofluoric acid is present in purge water – skin and eye contact hazard exists. | Prevent venting of possible PFIB gas. Bubble through water solution (See diagram in Appendix E) 2 persons must be present at all times during the operation Perform transfer operation with as much natural ventilation, and in as large a air volume as possible. Do not perform this procedure in a confined space or poorly ventilated large space. Supplement ventilation by using fans blowing over apparatus into open space. Only perform this transfer operation when the Fluorinert is within 5 deg C of normal Bld D temperature (20 deg C) Use dry nitrogen to purge MV housing, pressurize to no more than 5 psi. Install pressure gage between MV housing and recovery drum. Purge 3 volumes of MV housing through closed system to recovery drum and purge apparatus. Hydrolyze sample to convert to hydrofluoric acid; use HF probe to quantify. Vent scrubbed purge gas to building exhaust, 100% exhaust – no return Avoid skin and eye contact with purge water that tests positive for HF. Wear HF resistant gloves and safety glasses/goggles. Mitigate potential skin and eye contact hazard by adding sodium bicarbonate and calcium carbonate to purge vessel until the pH is > 3.0. |
| Draining system of FC-77 | Potential spill – exposure | Use closed liquid transfer system to drain MV housing. (see Appendix E) Wear laboratory safety glasses during transfer Have spill kit nearby to handle any leaks. See emergency procedures. |
| Re-use of FC-77 | Potential for contamination with PFIB and/or HF (due hydrolysis of PFIB in presence of water contamination); potential skin/eye contact hazard and/or inhalation hazard. Potential spill or back strain | Use mechanical pump, closed system to transfer FC-77 from recovery drum, though the FC-77 Wash apparatus (see Appendix F) to MV housing; inlet for transfer hose/pipe should be placed near bottom of recovery drum (to take advantage of greater specific gravity of FC-77 in contrast to water) to avoid contaminated water phase. Test pH of wash water and test for F ion. If pH > 2.0; raise pH with calcium carbonate/sodium carbonate to > 4.0. Wear laboratory safety glasses during the transfer Use mechanical pump/transfer system to refill the MV or LV housing. |

VII.  Emergency Procedures

All employees involved in the MARS project and involved in the handling and use of FC-77 must be trained on proper, safe responses to emergencies including spill, fire, and first aid/medical.

| Emergency Event | Hazard | Safety Procedure |
| --- | --- | --- |
| Spill response - < 1 gallon of unused FC-77 | Slip and fall Skin & eye contact – irritant | Avoid stepping in liquid; drop absorbent pads onto spill Wear gloves and eye protection, goggles. Absorb spilled liquid; place contaminated absorbents into labeled, sealed container for waste disposal; see below. |
| Spill response > 1 gallon (of unused FC-77) | Slip and fall Vapor exposure - irritant | First priorities: Safety, Isolate area, Notify ERT See above Ventilate space with confined space fan Drop vapor barrier spill pads onto top of spill |
| Spill response < 1 liter (Used FC-77) | Assume presence of PFIB, inhalation hazard | Use exhaust ventilation during MV or LV housing draining. Drop vapor barrier absorbents onto spill. Wait 15 minutes, then clean up liquid FC-77. |
| Spill response > 1 liter (Used FC-77) | Assume presence of PFIB, inhalation hazard Environmental contamination – water pollution (sinker) | Use exhaust ventilation during PFIB vessel draining. SIN: Provide for personnel Safety/evacuate immediate area; Isolate – deny entry to others; Notify ERT; Contact outside clean up contractor. Keep out of storm drains and water ways – FC77 sinks (difficult to recover) |
| Possible/suspected excess heating of FC-77 above | Formation of PFIB – inhalation hazard/toxic | Follow procedures above for draining FC-77 from MV housing. Transfer fluid with closed system. Use local exhaust to capture fugitive emissions from receiving container. Collect for determination as to whether or not purge solution is hazardous waste. |
| Fire | Toxic inhalation hazard | Immediately evacuate the area, close doors. Pull closest fire alarm. If safe to do so, use fire extinguisher in very early stage of fire only. |
| Shock/Electrocution | Potential shock/electrocution | Cut the electrical power to the equipment – Do Not Touch victim or equipment without shutting off the power Check for pulse and respiration – Call 911/for help – start CPR as indicated. |

VIII.  Waste Handling Procedures

Trace contaminants within the Fluorinert do not automatically render liquid a hazardous waste.  Only when MARS program personnel deem the Fluorinert to no longer meet the performance specifications and, as such, has no further use at MBARI, does the Fluorinert become a waste and, as such, a hazardous waste.

Collect waste FC-77 in labeled containers, drums.  Select the size of container for volume of waste collected.  Label as “Hazardous Waste” indicate date of collection and contents, i.e., waste Fluorinert.  Contact Patrick Whaling for correct labels and request for transfer of waste to Hazardous Materials/Waste Building.

For waste purge water, determine the pH and presence/absence of HF (via fluoride ion probe).  If pH is > 2.0, then the waste purge water is not hazardous waste and may be discharged to a sanitary sewer (not to storm drain).

If the pH is < 2.0, then the purge water is classified as hazardous waste and must be containerized and labeled accordingly.  Label as “Hazardous Waste”, indicate the date of collection and contents, i.e., waste water, pH 2.0.  Contact Patrick Whaling for correct labels and request for transfer of waste to Hazardous Materials/Waste Building.

Appendix A

Hazard Review – Fluorinert

MONTEREY BAY AQUARIUM RESEARCH INSTITUTE

Hazard Review – Fluorinert, FC 77

July 10, 2007 (update 10-15-07)

Background:	Fluorinert, FC 77, is a halogenated hydrocarbon liquid that is used as a dielectric in various pieces of electrical equipment.  It is used, in part, because it is stable under elevated temperatures.

Hazards:  Halogenated hydrocarbons as a chemical group share some general physical properties; these include stable under elevated temperatures and nonflammable.  Halogenated hydrocarbons, including FC 77, do, however, breakdown under fire conditions to toxic gases.  Vapors exposed to open flame, electrical arc or strong ultraviolet light will also decompose into toxic gases.

Despite their higher molecular weights, these materials are volatile.  As such they pose varying inhalation hazards.  The toxicity of the halogenated hydrocarbons varies significantly among the group.  FC 77 is not significantly toxic under normal use; the toxicity hazard is upon decomposition.  Thermal decomposition of FC-77 can produce perfluoroisobutylene and hydrofluoric acid.

The high volatility of the halogenated hydrocarbons does pose a risk of asphyxiation due to oxygen displacement when the liquids are spilled.  The risk increases if the spill occurs in small, enclosed spaces without sufficient ventilation to dissipate the vapors.

Halogenated hydrocarbons also have high specific gravity values, being much heavier than water for equal volumes.  FC 77 weighs almost 14 ½ pounds per gallon in contrast to water at 8 pounds per gallon.  Consequently, FC 77 poses a potential back and or shoulder injury risk.

Safety Practices:

- The dominate risk under normal use is for back and/or shoulder injury.  Use hand trucks to move containers of 5 gallons or more.  Purchase/use in containers of smallest practical volume.  Get assistance when moving multiple containers.  Use proper lifting techniques.  Use hand pumps or mechanical pumps to transfer liquid when feasible versus hand pouring.

- Avoid open flame, spark, electrical arc, strong UV light.

- Adequately ventilate use areas and increase ventilation for major spills, > 1 gallon.

- Avoid mixing with strong oxidizers; store/segregate away from oxidizers.

Ref:  3M MSDS, Fluorinert FC77, 7/19/2006

Appendix B

3M Material Safety Data Sheet, MSDS: Fluorinert

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 1 of 8

Material Safety Data Sheet

Copyright, 2006, 3M Company. All rights reserved. Copying and/or downloading of this information for the purpose of properly

utilizing 3M products is allowed provided that: (1) the information is copied in full with no changes unless prior written agreement is

obtained from 3M, and (2) neither the copy nor the original is resold or otherwise distributed with the intention of earning a profit

thereon.

SECTION 1: PRODUCT AND COMPANY IDENTIFICATION

PRODUCT NAME: FC-77 FLUORINERT Brand Electronic Liquid

MANUFACTURER: 3M

DIVISION: Electronics Markets Materials Division

ADDRESS: 3M Center

St. Paul, MN 55144-1000

EMERGENCY PHONE: 1-800-364-3577 or (651) 737-6501 (24 hours)

Issue Date: 07/19/2006

Supercedes Date: 07/10/2006

Document Group: 10-3791-0

Product Use:

Intended Use: For industrial use only. Not intended for use as a medical device or drug.

Specific Use: Testing Fluid or Heat Transfer Fluid for Electronics

SECTION 2: INGREDIENTS

Ingredient C.A.S. No. % by Wt

PERFLUORO COMPOUNDS, (PRIMARILY COMPOUNDS WITH 8

CARBONS)

86508-42-1 100

SECTION 3: HAZARDS IDENTIFICATION

3.1 EMERGENCY OVERVIEW

Specific Physical Form: Liquid

Odor, Color, Grade: Colorless, odorless liquid.

General Physical Form: Liquid

Immediate health, physical, and environmental hazards:

3.2 POTENTIAL HEALTH EFFECTS

Eye Contact:

Contact with the eyes during product use is not expected to result in significant irritation.

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 2 of 8

Skin Contact:

Contact with the skin during product use is not expected to result in significant irritation.

Inhalation:

If thermal decomposition occurs:

May be harmful if inhaled.

Ingestion:

No health effects are expected.

3.3 POTENTIAL ENVIRONMENTAL EFFECTS

This compound is completely fluorinated (perfluorinated), or it contains perfluorinated portions. Perfluoroalkyl groups resist

degradation in most natural environments. This low-solubility substance has insignificant toxicity to aquatic organisms (Lowest LL50

or EL50 is >1000 mg/L). LL50 (Lethal Level) and EL50 are similar to LC50 and EC50, but tests the water phase from incompletelymiscible

mixtures. Take precautions to prevent direct release of this substance to the environment. ATMOSPHERIC FATE:

Perfluoro compounds (PFCs) are photochemically stable and expected to persist in the atmosphere for more than 1000 years. PFCs

have high global warming potential, exceeding 7000 (100-yr-ITH,calculated using the IPCC 2001 methodology). The Ozone

Depletion Potential (ODP) is Zero.

SECTION 4: FIRST AID MEASURES

4.1 FIRST AID PROCEDURES

The following first aid recommendations are based on an assumption that appropriate personal and industrial hygiene practices are

followed.

Eye Contact: Flush eyes with large amounts of water. If signs/symptoms persist, get medical attention.

Skin Contact: Wash affected area with soap and water. If signs/symptoms develop, get medical attention.

Inhalation: If signs/symptoms develop, remove person to fresh air. If signs/symptoms persist, get medical attention.

If Swallowed: No need for first aid is anticipated.

SECTION 5: FIRE FIGHTING MEASURES

5.1 FLAMMABLE PROPERTIES

Autoignition temperature Not Applicable

Flash Point Not Applicable

Flammable Limits - LEL [Details: Nonflammable]

Flammable Limits - UEL [Details: Nonflammable]

5.2 EXTINGUISHING MEDIA

Material will not burn.

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 3 of 8

5.3 PROTECTION OF FIRE FIGHTERS

Special Fire Fighting Procedures: Water may be used to blanket the fire. Exposure to extreme heat can give rise to thermal

decomposition. Wear full protective equipment (Bunker Gear) and a self-contained breathing apparatus (SCBA).

Unusual Fire and Explosion Hazards: No unusual fire or explosion hazards are anticipated. No unusual effects are anticipated

during fire extinguishing operations. Avoid breathing the products and substances that may result from the thermal decomposition of

the product or the other substances in the fire zone. Keep containers cool with water spray when exposed to fire to avoid rupture.

Note: See STABILITY AND REACTIVITY (SECTION 10) for hazardous combustion and thermal decomposition

information.

SECTION 6: ACCIDENTAL RELEASE MEASURES

Accidental Release Measures: Observe precautions from other sections. Call 3M- HELPS line (1-800-364-3577) for more

information on handling and managing the spill. Evacuate unprotected and untrained personnel from hazard area. The spill should be

cleaned up by qualified personnel. Ventilate the area with fresh air. Contain spill. Working from around the edges of the spill

inward, cover with bentonite, vermiculite, or commercially available inorganic absorbent material. Mix in sufficient absorbent until it

appears dry. Collect as much of the spilled material as possible. Clean up residue with an appropriate organic solvent. Read and

follow safety precautions on the solvent label and MSDS. Place in a metal container approved for transportation by appropriate

authorities. Seal the container. Dispose of collected material as soon as possible.

In the event of a release of this material, the user should determine if the release qualifies as reportable according to

local, state, and federal regulations.

SECTION 7: HANDLING AND STORAGE

7.1 HANDLING

For industrial or professional use only. Avoid breathing of vapors, mists or spray. Do not breathe thermal decomposition products.

No smoking: Smoking while using this product can result in contamination of the tobacco and/or smoke and lead to the formation of

the hazardous decomposition products mentioned in the Reactivity Data section of this MSDS. Store work clothes separately from

other clothing, food and tobacco products.

7.2 STORAGE

Keep container in well-ventilated area. Keep container tightly closed. Store away from heat. Store out of direct sunlight.

SECTION 8: EXPOSURE CONTROLS/PERSONAL PROTECTION

8.1 ENGINEERING CONTROLS

Use with appropriate local exhaust ventilation. Provide appropriate local exhaust when product is heated. For those situations where

the fluid might be exposed to extreme overheating due to misuse or equipment failure, use with appropriate local exhaust ventilation

sufficient to maintain levels of thermal decomposition products below their exposure guidelines.

8.2 PERSONAL PROTECTIVE EQUIPMENT (PPE)

8.2.1 Eye/Face Protection

Avoid eye contact.

The following eye protection(s) are recommended: Safety Glasses with side shields.

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 4 of 8

8.2.2 Skin Protection

Gloves are not required when product is uncontaminated and at room temperature.

Avoid skin contact with extremely cold or hot product. Wear appropriate gloves when handling this product to protect skin from low

or high temperatures.

If the product becomes contaminated during use, select and use gloves and/or protective clothing to prevent skin contact based on the

results of an exposure assessment. Consult with your glove and/or protective clothing manufacturer for selection of appropriate

compatible materials.

8.2.3 Respiratory Protection

Avoid breathing of vapors, mists or spray. Under normal use conditions, airborne exposures are not expected to be significant enough

to require respiratory protection.

If thermal degradation products are expected, use fullface supplied air respirator.

8.2.4 Prevention of Swallowing

Not applicable.

8.3 EXPOSURE GUIDELINES

None Established

SECTION 9: PHYSICAL AND CHEMICAL PROPERTIES

Specific Physical Form: Liquid

Odor, Color, Grade: Colorless, odorless liquid.

General Physical Form: Liquid

Autoignition temperature Not Applicable

Flash Point Not Applicable

Flammable Limits - LEL [Details: Nonflammable]

Flammable Limits - UEL [Details: Nonflammable]

Boiling point 90 - 107 ºC

Density 1.8 g/ml

Vapor Density Approximately 14 [@ 20 ºC] [Ref Std: AIR=1]

Vapor Pressure Approximately 42 mmHg [@ 20 ºC]

Specific Gravity Approximately 1.8 [Ref Std: WATER=1]

pH Not Applicable

Melting point Not Applicable

Solubility in Water Nil

Evaporation rate > 1 [Ref Std: BUOAC=1]

Volatile Organic Compounds [Details: Exempt]

Percent volatile Approximately 100 %

VOC Less H2O & Exempt Solvents [Details: Exempt]

Viscosity 0.8 centistoke [@ 20 ºC]

SECTION 10: STABILITY AND REACTIVITY

Stability: Stable.

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 5 of 8

Materials and Conditions to Avoid: Finely divided active metals; Alkali and alkaline earth metals; Heat(greater than 200 ºC)

Hazardous Polymerization: Hazardous polymerization will not occur.

Hazardous Decomposition or By-Products

Substance Condition

Hydrogen Fluoride At Elevated Temperatures - greater than 200 ºC

Perfluoroisobutylene (PFIB) At Elevated Temperatures - greater than 200 ºC

Hazardous Decomposition: Hydrogen fluoride has an ACGIH Threshold Limit Value of 3 parts per million (as fluoride) as a Ceiling

Limit and an OSHA PEL of 3 ppm of fluoride as an eight hour Time-Weighted Average and 6 ppm of fluoride as a Short Term

Exposure Limit. The odor threshold for HF is 0.04 ppm, providing good warning properties for exposure.

SECTION 11: TOXICOLOGICAL INFORMATION

Product-Based Toxicology Information:

A Material Toxicity Summary Sheet (MTSS) has been developed for this product. Please contact the address listed on the first page

of this MSDS to obtain a copy of the MTSS for this product.

Please contact the address listed on the first page of the MSDS for Toxicological Information on this material and/or its

components.

SECTION 12: ECOLOGICAL INFORMATION

ECOTOXICOLOGICAL INFORMATION

Test Organism Test Type Result

Water flea, Daphnia magna 48 hours Effect Concentration 50% >1500 mg/l

Fathead Minnow, Pimephales promelas 96 hours Lethal Concentration 50% >1000 mg/l

CHEMICAL FATE INFORMATION

Test Type Result Protocol

20 days Biological Oxygen Demand Nil

Chemical Oxygen Demand Nil

SECTION 13: DISPOSAL CONSIDERATIONS

Waste Disposal Method: Reclaim if feasible. As a disposal alternative, incinerate in an industrial or commercial facility in the

presence of a combustible material. Combustion products will include HF. Facility must be capable of handling halogenated

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 6 of 8

materials.

To reclaim or return, check product label for contact.

EPA Hazardous Waste Number (RCRA): Not regulated

Since regulations vary, consult applicable regulations or authorities before disposal.

SECTION 14:TRANSPORT INFORMATION

ID Number(s):

98-0204-0701-5, 98-0211-1773-8, 98-0211-1774-6, 98-0211-3999-7, 98-0211-6447-4, 98-0211-8800-2, 98-0211-8807-7, 98-

0211-9371-3, 98-0212-3124-0, 98-0212-3183-6, ZF-0002-0105-1, ZF-0002-0106-9, ZF-0002-0320-6, ZF-0002-0389-1, ZF-0002-

1139-9, ZF-0002-1164-7, ZF-0002-1445-0, ZF-0002-4132-1

Not regulated per U.S. DOT, IATA or IMO.

These transportation classifications are provided as a customer service. As the shipper YOU remain responsible for

complying with all applicable laws and regulations, including proper transportation classification and packaging. 3M's

transportation classifications are based on product formulation, packaging, 3M policies and 3M's understanding of applicable

current regulations. 3M does not guarantee the accuracy of this classification information. This information applies only to

transportation classification and not the packaging, labeling, or marking requirements. The original 3M package is certified

for U.S. ground shipment only. If you are shipping by air or ocean, the package may not meet applicable regulatory

requirements.

SECTION 15: REGULATORY INFORMATION

US FEDERAL REGULATIONS

Contact 3M for more information.

311/312 Hazard Categories:

Fire Hazard - No Pressure Hazard - No Reactivity Hazard - No Immediate Hazard - No Delayed Hazard - No

STATE REGULATIONS

Contact 3M for more information.

CHEMICAL INVENTORIES

The components of this product are in compliance with the chemical notification requirements of TSCA.

All applicable chemical ingredients in this material are listed on the European Inventory of Existing Chemical Substances (EINECS),

or are exempt polymers whose monomers are listed on EINECS.

The components of this product are listed on the Canadian Domestic Substances List.

The components of this product are listed on the Australian Inventory of Chemical Substances.

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 7 of 8

The components of this product are listed on Japan's Chemical Substance Control Law List (also known as the Existing and New

Chemical Substances List.)

Contact 3M for more information.

INTERNATIONAL REGULATIONS

Contact 3M for more information.

This MSDS has been prepared to meet the U.S. OSHA Hazard Communication Standard, 29 CFR 1910.1200.

SECTION 16: OTHER INFORMATION

NFPA Hazard Classification

Health: 3 Flammability: 0 Reactivity: 0 Special Hazards: None

National Fire Protection Association (NFPA) hazard ratings are designed for use by emergency response personnel to address the hazards that are

presented by short-term, acute exposure to a material under conditions of fire, spill, or similar emergencies. Hazard ratings are primarily based on the

inherent physical and toxic properties of the material but also include the toxic properties of combustion or decomposition products that are known to

be generated in significant quantities.

HMIS Hazard Classification

Health: 0 Flammability: 0 Reactivity: 0 Protection: X - See PPE section.

Hazardous Material Identification System (HMIS(r)) hazard ratings are designed to inform employees of chemical hazards in the workplace. These

ratings are based on the inherent properties of the material under expected conditions of normal use and are not intended for use in emergency

situations. HMIS(r) ratings are to be used with a fully implemented HMIS(r) program. HMIS(r) is a registered mark of the National Paint and

Coatings Association (NPCA).

Revision Changes:

Section 14: ID Number(s) was modified.

DISCLAIMER: The information in this Material Safety Data Sheet (MSDS) is believed to be correct as of the date issued. 3M

MAKES NO WARRANTIES, EXPRESSED OR IMPLIED, INCLUDING, BUT NOT LIMITED TO, ANY IMPLIED WARRANTY

OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE OR COURSE OF PERFORMANCE OR USAGE OF

TRADE. User is responsible for determining whether the 3M product is fit for a particular purpose and suitable for user's method of

use or application. Given the variety of factors that can affect the use and application of a 3M product, some of which are uniquely

within the user's knowledge and control, it is essential that the user evaluate the 3M product to determine whether it is fit for a

particular purpose and suitable for user's method of use or application.

3M provides information in electronic form as a service to its customers. Due to the remote possibility that electronic transfer may

have resulted in errors, omissions or alterations in this information, 3M makes no representations as to its completeness or accuracy.

In addition, information obtained from a database may not be as current as the information in the MSDS available directly from 3M.

3M MATERIAL SAFETY DATA SHEET FC-77 FLUORINERT Brand Electronic Liquid 07/19/2006

_________________________________________________________________________________________________

Page 8 of 8

3M MSDSs are available at www.3M.com

Appendix C

International Chemical Safety Card: Perfluoroisobutylene, PFIB

# International Chemical Safety Cards PERFLUOROISOBUTYLENE; ICSC: 1216. Octafluoroisobutylene 1,1,3,3,3-Pentafluoro-2-trifluoromethyl-1-propene Octafluoro-sec-butene C4F8 Molecular mass: 200.0 ICSC # 1216 CAS # 382-21-8 RTECS # UD1800000 April 21, 2004 Peer reviewed. TYPES OF HAZARD/ EXPOSURE; ACUTE HAZARDS/ SYMPTOMS; PREVENTION; FIRST AID/ FIRE FIGHTING. FIRE; In case of fire in the surroundings: use appropriate extinguishing media.. EXPLOSION. EXPOSURE; STRICT HYGIENE!. •INHALATION; Sore throat. Cough. Nausea. Headache. Weakness. Shortness of breath. Laboured breathing. Symptoms may be delayed (see Notes).; Ventilation, local exhaust, or breathing protection.; Fresh air, rest. Half-upright position. Artificial respiration may be needed. Refer for medical attention.. •SKIN; Protective gloves.. •EYES; Safety spectacles.; First rinse with plenty of water for several minutes (remove contact lenses if easily possible), then take to a doctor.. •INGESTION. SPILLAGE DISPOSAL; STORAGE; PACKAGING & LABELLING. Evacuate danger area! Consult an expert! Ventilation. Personal protection: self-contained breathing apparatus.; R: S:. SEE IMPORTANT INFORMATION ON BACK. ICSC: 1216; Prepared in the context of cooperation between the International Programme on Chemical Safety & the Commission of the European Communities (C) IPCS CEC 1994. No modifications to the International version have been made except to add the OSHA PELs, NIOSH RELs and NIOSH IDLH values...

# International Chemical Safety Cards PERFLUOROISOBUTYLENE; ICSC: 1216. I M P O R T A N T D A T A; PHYSICAL STATE; APPEARANCE: COLOURLESS GAS. PHYSICAL DANGERS: CHEMICAL DANGERS: OCCUPATIONAL EXPOSURE LIMITS: TLV: 0.01 ppm (Ceiling value) (ACGIH 2004). MAK not established.; ROUTES OF EXPOSURE: The substance can be absorbed into the body by inhalation. INHALATION RISK: A harmful concentration of this gas in the air will be reached very quickly on loss of containment. EFFECTS OF SHORT-TERM EXPOSURE: The substance is irritating to the respiratory tract Inhalation of this gas may cause lung oedema (see Notes). Exposure may result in death. The effects may be delayed. Medical observation is indicated. EFFECTS OF LONG-TERM OR REPEATED EXPOSURE:.. PHYSICAL PROPERTIES; Boiling point: 7°C Density: 1.6 g/l.. ENVIRONMENTAL DATA. N O T E S. This substance is formed as a by-product in tetrafluoroethylene production and during thermal degradation of polytetrafluoroethylene (PTFE/Teflon(R)) at approximately 425°C. The occupational exposure limit value should not be exceeded during any part of the working exposure. The symptoms of lung oedema often do not become manifest until a few hours have passed and they are aggravated by physical effort. Rest and medical observation are therefore essential. Immediate administration of an appropriate inhalation therapy by a doctor or a person authorized by him/her, should be considered.. ADDITIONAL INFORMATION. ICSC: 1216; PERFLUOROISOBUTYLENE. (C) IPCS, CEC, 1994..

IMPORTANT LEGAL NOTICE:; Neither NIOSH, the CEC or the IPCS nor any person acting on behalf of NIOSH, the CEC or the IPCS is responsible for the use which might be made of this information. This card contains the collective views of the IPCS Peer Review Committee and may not reflect in all cases all the detailed requirements included in national legislation on the subject. The user should verify compliance of the cards with the relevant legislation in the country of use. The only modifications made to produce the U.S. version is inclusion of the OSHA PELs, NIOSH RELs and NIOSH IDLH values..

Appendix D

Toxicology of Perfluorisobutylene

PFIB Toxicology

Editor’s Note: The following is a review of much of the literature on the toxicology of PFIB. Although listed in Schedule 2 of the CWC, there is relatively little written in the usual military chemical books about PFIB, compared to the "classic" CW agents. Much of the literature discussion appeared in occupational medicine journals in the 1960s and 1970s. In the interests of better understanding of common medical issues in CBW, ASA is happy to present this article by Drs. Bajgar and Patocka. Toxicology of Perfluoroisobutene by Jiri Patocka and Jiri Bajgar The Department of Toxicology, Military Medical Academy 500 01 Hradec Kr‡lovŽ, Czech Republic. E-mail: patocka@pmfhk.cz and bajgar@pmfhk.cz Introduction Perfluoroisobutene (PFIB, 1,1,1,3,3-penta fluoro-2-trifluoro methylpropene, CAS No. 3812-21-8) is a fluoro-olefin produced by thermal decomposition of polytetrafluoroethylene (PTFE), e.g., Teflon [1]. Overheating of PTFE generates fumes of highly toxic PFIB and poses a serious health hazard to the human respiratory tract. PFIB is approximately ten times as toxic as phosgene [2]. Inhalation of this gas can cause pulmonary edema, which can lead to death. PFIB is included in Schedule 2 of the Chemical Weapons Convention (CWC), as a result of the prompting by one delegation to the Conference on Disarmament [3]. The aim of the inclusion of chemicals, such as PFIB was to cover those chemicals, which would pose a high risk to the CWC. Subsequently PFIB, specifically, was included in the final text of the CWC. Chemistry PFIB is a strong electrophile, which reacts with all nucleophiles [4]. The high electrophilicity of PFIB is a result of the strong electron-attracting effects of the fluorine atoms of the trifluoromethyl groups and the conjugation of the fluorine’s p electrons with the double bond of the vinyl group. Several reactive intermediate species were identified in the reaction of PFIB with nitrone and nitroso spin trap agents, and, some of the expected reactive nucleophiles in vivo include amines, alcohols and especially thiols [5]. PFIB decomposes rapidly when dissolved in water, forming various reactive intermediates and fluorophosgene, which then decomposes into carbon dioxide, a radical anion and hydrogen fluoride [6]. PFIB is a gas with a boiling point of 7.0çC at one atm and a gas density of 8.2 g/L [9]. The synthesis of PFIB from fluorodichloromethane is given in Fig. 1. Toxicology The toxicity of PFIB may be correlated with its susceptibility to nucleophilic attack and the generation of reactive intermediates [1]. This is similar to the toxicity of other fluoro-olefins; their toxicity is directly proportional to the reactivity of that olefin with nucleophiles [7, 8]. Acute Toxicity The median lethal concentration (LC50) in single exposures of rats was 0.5 ppm. The intoxicated rats either died with gross pathological signs of pulmonary congestion or recovered with no apparent residual effects. The 15-second LC50 was 361 ppm and the 10-minute LC50 was 17 ppm [9]. Similar high acute toxicity following inhalation was seen in other species with a two hour LC50 in mice reported to be either 1.6 ppm [9] or 0.98 ppm [10], in rabbits either 4.3 ppm [10] or 1.2 ppm [11], in guinea-pigs 1.05 ppm [10] and in cats 3.1 ppm [10]. In experiments in which rats were exposed to a concentration of 12.2 ppm for 10 min, an unusual postexposure latency period of approximately 8 hours was observed prior to the occurrence of pulmonary edema [12]. Repeated Dose Toxicity The information on repeated dose inhalation studies of PFIB are not generally available. According to Kennedy [13], rats exposed to 0.1 ppm, six hours per day, five days per week for two weeks showed no compound-related pathological changes and only mild respiratory impairment and restlessness during their exposure. A repeat study using the same experimental conditions (0.1 ppm) found no effects in rats [14]. Human Toxicity Pyrolytic products of PTFE heated below 500çC may be dangerous [15].[Editor’s note: this has been called "polymer fume fever."] Five workers accidentally exposed to a gas containing 2 percent PFIB reported irritation of the respiratory tract within 24 h of exposure. The lung irritation was manifested by cough in all cases. The patients developed headache, cough, substernal pain, dyspnoea and fever within the first hour following exposure. The symptoms became worse at six to eight hours after exposure. Also choking or shortness of breath was observed in a majority of the patients. The condition of the patients began to improve on the fifth day and they were discharged from the hospital after two to three weeks. One patient developed a respiratory infection, which required his stay in hospital to be extended to about eight weeks. All the patients were shown to have pulmonary edema and this was confirmed at post mortem on two patients died. One died after 11 days after exposure, the other died after 13 days [16, 17]. According to Kennedy [14], one worker exposed to PFIB for three minutes reported strong subjective symptoms of bad odor, bad taste in the mouth, nausea and weakness. On returning to fresh air, the worker recovered and had no further symptoms. Half an hour later, a concentration of 0.04 ppm of PFIB was measured in the exposure area. The latency period for PFIB injury is one to four hours until pulmonary edema symptoms appear. In many cases, pulmonary edema clears up in about 72 hours, with little long-term damage [27]. Genetic Toxicity and Carcinogenicity No information of either genetic toxicity or carcinogenicity was found. Environmental Toxicity No officially available studies on the environmental effects of PFIB have been found. The concentration of PFIB in air can be determined [18] and probably 0.1 ppm is the maximum air concentration (cont. p. 16 "PFIB") ("PFIB" from p. 15) below which nearly all individuals could be exposed for up to one hour without serious adverse health effects or symptoms [13]. Pathology The histopathology of rat lung has been studied after an acute exposure to PFIB at a concentration of 78 ppm for 1.5 min. Within 5 min of exposure, changes to the bronchioles and peribronchial alveoli were observed which took the form of alterations to cilial structure, increased pinocytosis with occasional vesicle formation of type I alveolar epithelial cells. The gradual development of pulmonary edema was visible histologically two to three hours post exposure, with death occurring from seven hours onwards. Animals sacrificed at 24 hours post exposure showed evidence of widespread pulmonary edema and alveolar interstitial infiltration by lympho mononuclear cells and macrophages [19]. In other experiments, PFIB induced pulmonary edema involving a translocation of blood compartment proteins into the lung’s alveolar compartment. By high-performance capillary electrophoresis of proteins from the fluid lining of the lungs of rats exposed to PFIB was estimated that albumin, transferrin and IgG are three major proteins translocated into the alveolar space [20]. Pretreatment and Treatment The PFIB exposure caused an immediate depletion of intracellular lung cysteine and glutathione. Therefore several cysteine esters and N-acetylcysteine were used as thiol pretreatment to increase the level of intracellular thiols and have been shown to protect against a lethal exposure of PFIB [21]. Oral N-acetylcysteine , which is used as a mucolytic in chronic obstructive pulmonary disease, as well as in diseases which are complicated by the production of viscous mucus [22, 23], has shown protection against inhalation of PFIB in rats [24]. Protection against the lethal effect of inhaled PFIB has been shown when N-acetylcysteine has been orally administered 4, 6 or 8 hours before gas exposure and the duration of protection has been related to the duration of increased levels of cysteine, glutathione and N-acetylcysteine in the plasma [24]. The treatment of PFIB intoxication is based on edema reduction by administration of diuretics. In experiments on rats, the diuretics furosemide and torasemide reduced the lung edema and the pattern and severity of the pathological changes associated with inhalation of PFIB and delayed the time to death [25]. Conclusions Perfluoroisobutene (PFIB) is a hydrophobic reactive gas produced by pyrolysis of polytetrafluoroethane that induces pulmonary edema similar to that induced by phosgene when inhaled. PFIB is highly toxic, approximately ten times as toxic as phosgene and can be very dangerous for humans. Oral administration of N-acetylcysteine appears to be a good protective drug against the lethal effect of inhaled PFIB. References 1. Zeifman, Y.B., Ter-Gabrielyan, N.P., Knunyants, I.L. The Chemistry of Perfluoroisobutylene. Uspekhi Khimii, 1984; 53: 431-461. 2. Oberdorster, G., Ferin, J., Gelein, J., Finkelstein, R., Baggs, R., Effects of PTFE Fumes in the Respiratory Tract: A Particle Effect? Aerospace Medical Assiciation 65th Annual Scientific Meeting, 1994; 538: A52. 3. CD/CW/WP.239. Verification of the Nonproduction of Chemical Weapons: An Illustrative Example of the Problem of Novel Toxic Chemicals. 12 April 1989. 4. England, D.C., Krespan, C.G. Fluoroketenes. I. Bis(trifluoromethyl)ketene and Its Reaction with Fluoride Ion. J Am Chem Soc, 1966; 88: 5582-5587. 5. Arroyo, C.M. The Chemistry of Perfluoroisobutylene (PFIB) with Nitrone and Nitroso Spin Traps: an EPR/Spin Trapping Study. Chem Biol Interact 1997; 105: 119-129. 6. Lailey, A.F., Hill, L., Lawston, I.W., Stanton, D., Upshall, D.G. Protection by Cysteine Esters Against Chemically Induced Pulmonary Oedema. Biochem Pharmacol 1991; 42: PS47-52. 7. Cook, E.W., Pierce, J.S. Toxicology of Fluoro-Olefins. Nature 1973; 242: 337-338. 8. Clayton, J.W. Toxicology of the Fluoroalkenes. Review and Research Needs. Environ Health Perspect 1977; 21: 255-267. 9. Smith, L.W., Gardner, R.J., Kennedy, G.L., Jr. Short-Term Inhalation Toxicity of Perfluoroisobutylene. Drug Chem Toxicol 1982; 5: 295-303. 10. Karpov, B.D. Determination of Upper and Lower Parameters of Perfluoroisobutylene Toxicity. Tr. Leningr Sanit Gig Med Inst 1975; 30: 111-120. 11. Paulet, G., Bernard, J.P. High Boilers Appearing During the Production of Polyfluorethylene. Biol Med 1968; 57: 247-301. 12. Lehnert, B.E., Archuleta, D., Gurley, L.R., Session, W., Behr, M.J., Lehnert, N.M., Stavert, D.M. Exercise Potentiation of Lung Injury Following Inhalation of a Pneumoedematogenic Gas: Perfluoroisobutylene. Exp Lung Res 1995; 21: 331-350. 13. Kennedy, G.L., Jr. Toxicology of Fluorine Containing Monomers. Crit Rev Toxicol 1990; 21: 149-170. 14. Kennedy, G.L., Jr., Geisen, R.J. Setting Occupational Exposure Limits for Perfluoroisobutylene, A Highly Toxic Chemical Following Acute Exposure. J Occup Med 1985; 27: 675-. 15. Waritz, R.S., Kwon, B.K. The Inhalation Toxicity of Pyrolysis Products of Polytetrafluoroethylene Heated Below 500 çC. Am Ind Hyg Assoc J 1968; 29: 19-26. 16. Unpublished data from DuPont Co., cited as Reference 15. 17. Danishevskii, S.L., Kochanov, M.M. Toxicity of Some Fluoroorganic Compounds. Gig Tr Prof Zabol 1961; 5: 3-8. 18. Marcali, K., Linch, A.L. Perfluoroisobutylene and Hexafluoropropene Determination in Air. Am Ind Hyg Assoc J 1966; 27: 360-368. 19. Brown, R.F., Rice, P. Electron Microscopy of Rat Lung Following a Single Acute Exposure to Perfluoroisobutylene (PFIB). A Sequential Study of the First 24 hours Following Exposure. Int J Exp Pathol 1991; 72: 437-450. 20. Gurley, L.R., Buchanan, J.S., London, J.E., Stavert, D.M., Lehnert, B.E. High Performance Capillary Electrophoresis of Proteins from the Fluid Lining of the Lungs of Rats Exposed to Perfluoroisobutylene. J Chromatogr 1991; 559: 411-429. 21. Lailey, A.F., Hill, L., Lawston, I.W., Stanton, D., Upshall, D.G. Protection by Cysteine Esters Against Chemically Induced Pulmonary Oedema. Biochem Pharmacol 1991; 42: Suppl. S47-S54. 22. Webb, W,R. Clinical Evaluation of a New Effective Mucolytic Agent (N-acetylcysteine). Am Rev Resp Disease 1962; 86: 115-116. 23. Ziment, I. Acetylcysteine: a Drug with an Interesting Past and a Fascinating Future. Respiration 1986; 50: 26-30. 24. Lailey, A.F. Oral N-acetylcysteine Protects Against Perfluoroisobutene Toxicity in Rats. Hum Exp Toxicol 1997; 16: 212-216. 25. Onyefuru, L.C., Upshall, D.G., Rice, P.. Effects of Furosemide, Torasemide and Controlled Fluid Intake on Perfluoroisobutene Induced Lung Oedema and Mortality. Arzneimittelforschung 1996;46: 283-287. 26. Brubaker, R.E., Pulmonary Problems Associated with the Use of Polytetraflurorethylene. J. Occup Med. 1977;19: 693-695.

For the Professional in Government and Industry with an interest in Nuclear, Biological and Chemical Defense, Disarmament and Verification; Emergency and Disaster Medical Planning; Industrial Health and Safety; and Environmental Protection

¯

Appendix E

Diagram of Recovery Drum and Purge & Trap Apparatus

Appendix F

Diagram of FC-77 Wash Apparatus