MARS Status March 30, 2010
Current Experiments - 2
· ACOMMS on port 3
· EK60 on port 6 – but turned off
Issues
MOBB 
MOBB site was where last trawl event occurred.  Current sensor and MOBB frame damaged.  3.6 km cable was ripped off.  Recovery for the MOBB cable will have to be scheduled.  
MVC Testing

Testing completed successfully with no incidents.  Lab access has been restored to normal.
MARS Lab UPS
The MARS lab UPS is marginally powered.  The new UPS has been received.  Need to schedule change over when time permits.  Probably be done when new servers are installed.
EOI Door Sensor

The contractor installed and wired most of the hardware necessary for monitoring the door switch at the end of the island.  He had to take some of the cards back for programming.  More time will need to be scheduled to finish the job.
LOOKING
LOOKING showed a maxed out ground fault when attached to MARS.  +48 volt feed shorted to case.  Failure analysis is on going including a check of the WNS GF detection circuits.
Future deployments/recoveries
MARS Cable Survey

Started 1/8/2010
ACOMMS
Recover 8/23/2010
Port 3
Lee Freitag @WHOI
FOCE

Deploy 4/7/2010
Recover August 22nd
Will attach to port 2

LOOKING (was OBS Seismometer)

Deploy 3/26/2010 maybe next week
Recover 9/30/2010
Will attach to port 1
John Orcutt @UCSD

EK60

Currently turned off.  Unit was turned off after EITS recovery.  

BPR/Tilt instrument for MARS
Deploy 6/30/2010
Recover 12/14/2010
Will attach to port 7

Bill Chadwick @NOAA

Scott Stalin @NOAA/PMEL

ESP

Deploy 11/30/2010

Recover – Not known yet

Will attach to port ?

Large Aperture Array

2011
NPS

Chinese MARS Node

Dejun Li @Zhejiang University, China

Application is in to NSF.  Plan to be on MARS for 3 months.
SAIC – Naval Hydrodynamics Division
Have expressed an interest in connecting to MARS from November 2010 until February 2011.
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