Test Tank Hazardous Voltage User Guide

Definitions:

ADCI: Association of Diving Contractors International

Energized equipment: Any equipment that is powered from an AC or DC source

GFCI: Ground Fault Circuit Interrupter

Hazardous voltage:

The new standard according to NFPA 70E 2018 edition is:

Any voltage above 50 V AC or DC

IMCA: International Marine Contractors Association

Minimum Safe Distance (MSD): The distance a diver can be from energized equipment and remain safe.

ROV: Remotely Operated Vehicle

Equipment energized with hazardous voltage when deployed in the tank will:

Have signage posted on all the entryways into the test tank area

Have signage posted on the rails of the tank

The signage shall read:

DANGER

Hazardous voltage present

Do not touch the water

If diving activities are planned contact:

Name of PI and Alternate

Date of activity Start/End

Use a GFCI if powered from a local source (local wall outlet)

(Trip current for these devices is usually found in the manufacturer’s literature)

Equipment energized with hazardous voltage and relying upon a ground return for detection of faults needs a ground connection on the frame of the experiment and to the ground reference plane of the Ground Fault Detection system; this is usually earth ground. In the case of ROVs powered from the ship, a ground reference will be tied to the frame of the ROV and to the grounding plate outside of the tank on the wall at the North East corner of the tank room. In the case of MARS experiments or the MARS node itself, a ground connection will be tied to the frame of the experiment or the node and “sea water” ground being defined as the point where the positive lead of the power supply is connected to earth.

In all cases, the safety ground shall be located as close as possible to the potential source of fault current, i.e. on the frame of the equipment itself and not a conductor elsewhere in the tank. We want to avoid the possibility of fault current passing through the water for any appreciable distance over a path which may pass through a diver.

IMCA provides calculations for the Minimum Safe Distance for diving around energized equipment based on the following formula:

Ss= (1 + {(I0 x 10-4) / Ib})1/2 - 1

Where:

Ss = approximate safe distance in seawater in meters

I0 = fault current

Ib = safe body current

AC Ib = 10 mA

DC Ib = 40 mA

For the case of Ventana, which is AC powered and has no human-rated ground fault circuit interrupter (GFCI):

I0 = 100 A

Ss = (1+ {(100 x 10-4)/.01})1/2 -1

= (1+ {(.01)/.01})1/2 -1

= (1+ {(1)})1/2-1

= (2)1/2 - 1

= 1.414 - 1

= 0.414 meters or approximately 1.4 feet

Examples of these calculations can be found in the “Code of Practice for the Safe Use of Electricity Under Water” which is available from MBARI’s Dive Officer (Kim Reisenbichler) or available for purchase here:

https://www.imca-int.com/publications/295/code-of-practice-for-the-safe-use-of-electricity-under-water/

Currently Ventana is the worst case for equipment used at MBARI because of its lack of human-rated GFCI. However, each piece of equipment needs to be evaluated prior to being installed in the tank and energized.

To keep casual users, visitors (tours etc.) and residents of the test tank area safe it is recommended that when equipment is energized and in the tank, it be situated in such a way as to create the minimum safe distance. This could be as simple as placing the equipment below the surface at a depth greater than the MSD.

Other considerations can be found in the ADCI guide for ROVs and Divers, section 9 shown below.

Diving with ROVs (https://www.adc-int.org/files/C11634_ADC%20Consensus%20Standard.pdf)

9.3 ROV AND DIVER OPERATIONAL PROCEDURES

9.3.1 INTRODUCTION

These recommended guidelines and procedures have been written to cover general guidelines regarding ROV-diver operations. These procedures are intended as guidelines for supervisors and operators. The essential factor to successfully and effectively conducting simultaneous ROV operations with diver intervention is COMMUNICATION. This word will be used often in these procedures. A clear line of communication between ROV crews and dive control is critical. A job safety analysis is a critical ingredient to assuring that all factors necessary to support the highest levels of safety have been considered.

9.3.2 DEFINITIONS

ROV Remote Operated Vehicle

TMS Tether Management System

LARS Launch and Recovery System

HPU Hydraulic Power Unit

FSW Feet Sea Water

MSW Meter Sea Water

9.3.3 ROV AND DIVE TEAM OPERATIONAL PROCEDURES

COMMUNICATION IS KEY TO SAFE AND EFFICIENT OPERATIONS.

9.3.3.1 PRE-DIVES

In addition to standard pre-dive briefings:

• It is important that all divers and dive supervisors are familiar with all aspects of the ROV.

• Location of thrusters, diver toolbox, manipulator arms, tether and camera locations should be areas of focus during this orientation.

• Camera location is important in order to emphasize to diving personnel the pilot’s field of vision.

• Tether is not to be used as a crossover/swim line for divers. • When mounting a diver toolbox on ROV, place it in a location that takes into consideration that most diving tools have lanyards on them. The diver needs to be able to access the toolbox and tools without getting lanyards or the divers themselves fouled in thrusters.

• Thruster location is important to divers. Divers will have pneumatics and tooling with lanyards. Even with thrusters nulled and the pilot holding a dead stick, thrusters will rotate. Divers need to secure all lanyards and pneumatic hoses before approaching an ROV.

.

9.3.3.2 SUBSEA OPERATIONS •

Before the ROV approaches a diver:

The diving supervisor must be notified.

Slow, easy movements of the ROV are required to prevent injury to diver.

When the diver approaches the ROV,

The diving supervisor must be notified as well as the ROV supervisor or pilot.

The ROV should stop all movements in order to allow the diver to approach.

When possible, the diver should approach from the front of the ROV, to allow the ROV pilot to view him or her.

If the ROV needs to dial in vertical thrust down, in order to hold position, the pilot should notify the dive supervisor that the thrusters are operating during diver’s approach.

Using manipulators with divers

The ROV should place the manipulator in such a position that diver can place a tool in the jaws.

The ROV pilot should then inform the diving supervisor that the manipulator jaw is closing. Once this is acknowledged, only then should the pilot close the ROV jaws.

The ROV should never try to take a tool from the diver; the diver must place the tool in the manipulator jaws to minimize manipulator movements.

The ROV tether should never be used for a diver crossover/swim-line.

When establishing a swim line for a diver:

After the ROV has acquired the hook for the crossover line, the diver should pay out the crossover line as the ROV flies to the connection point.

The diver should not let out excessive amounts of line during this operation. Line should be kept taut; if the pilot requires additional slack, he or she can then notify the dive supervisor.

After the crossover line is established, the diver should secure it so that excessive slack is not floating about for ROV to get tangled in thrusters.

Tag lines should be cut short or made ROV-friendly from surface.

ROV-friendly tag lines are ones that are removable from surface,

After tag lines have served their purpose, in over-boarding equipment.

If the diver is required to cut tag lines, the pieces cut off should be tied to a retrieval shackle, on down line.

The cut off pieces should then be recovered to surface for disposal, to mitigate the possibility of fouling ROV thrusters with rope floating about subsea. •

As stated earlier, the diver should not use the tether as a crossover line.

The diver should also try to go under the ROV tether. This will help prevent any entanglement problems with the diver, should the ROV lose hydraulics.

If the ROV is in a no-visibility situation: The diver should return to the stage or bell, if the ROV needs to perform tasks. If the ROV is not needed and the diver is required to stay on location, the ROV should go dead stick. The pilot should then inform the dive supervisor that the ROV is in a no-visibility situation and should remain clear from the diver. The ROV pilot should allow the ROV to rise above no-visibility to an area where visibility can be obtained. The ROV should not, for any reason, be flying in a no-visibility situation with a diver in the area. • The ROV pilot should be aware of all lines in the water. There will usually be at least one down line, running from the surface to the diver work location. Additionally, one or more crossover lines will also be present. This crossover line will run from the stage or bell (when applicable) to the work location