Mt Toro issues

1/12/2009

Mr. Tyler,

MBARI needs to have the following issues addressed at Mt Toro.

MBARI needs the rack space adjacent to its two existing racks.  Our lease gives us a 4’ x 6’ floor to ceiling space.

No antennas be installed adjacent to existing MBARI antennas and new installations be coordinated with MBARI to insure no interference is created.

48 hours notice is to be given when the AC power is to be interrupted for maintenance or other purposes.  

The HAM repeater antenna mounted near MBARI’s UHF antenna be moved down al least 20’ from its existing location.  All of the Ham’s repeater transmitters must have a intermod protection consisting of a circulator with the correct size load and harmonic filter.  Pass/Reject type duplexer cavities are not considered intermod protection.  

